| NOGRR Number | 062 | NOGRR Title | Require Voltage Ride-Through Capability for IRRs |
| --- | --- | --- | --- |
| Date Posted |  | March 3, 2011 |  |

| Nodal Operating Guide Section Requiring Revision | 2.9.1, Additional Voltage Ride-Through Requirements for Wind-powered Generation Resources |
| --- | --- |
| Protocol Section(s) Requiring Revision, if any | None. |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) | Urgent. Urgent status is needed in order to maintain reliability of the ERCOT System as more new Intermittent Renewable Resources (IRRs) are scheduled to be placed in service. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) proposes a requirement for Voltage Ride-Through (VRT) capability for new IRRs. |
| Reason for Revision | This NOGRR is being proposed for the following reasons: - Due to the expected IRRs to be placed in service over the next few years, lack of VRT capability could pose ERCOT reliability issues in the event of voltage excursions. - Concern of sudden voltage changes causing tripping of units without VRT capability. - Additionally, although the VRT study indicated there was no need to retrofit existing Wind-powered Generation Resources to add VRT capability, the concern remains if more units without VRT capability are placed in service, especially in west Texas where many existing WGRs do not have VRT capability. |
| Overall Market Benefit | System reliability is enhanced as new IRRs are added to the ERCOT System. Resource Entities will receive additional revenue due to decreased Outages resulting from increased ERCOT System reliability. |
| Overall Market Impact | Resource Entities will be required to design their Facilities to meet the new standard, which will result in some added capital cost. |
| Consumer Impact | Consumers will see reduced costs due to increased reliability of new generators with some potential that increased capital cost to Resource Entities of complying with the standard will be passed on to Consumers. |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Generation Entities will have to design their generation plants to meet the new standard, which will result in some added capital cost. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Maintain ERCOT System reliability as new IRRs are added to the. | Unknown. |
|  | 2 | Generation Entities will receive additional revenue due to decreased Outages resulting from increased ERCOT System reliability. | Unknown. |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores and Fred Huang |
| E-mail Address | iflores@ercot.com / shuang@ercot.com |
| Company | ERCOT |
| Phone Number | 512.248.6531 / 512.248.6665 |
| Cell Number |  |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512.248.4513 |

Proposed Guide Language Revision

- 2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall comply with Section 2.9, Voltage Ride-Through Requirements for Generation Resources, and the following:

(a)	Wind-powered Generation Resources (WGRs) that are part of a Standard Generation Interconnection Agreement (SGIA) signed on or after November 1, 2008 shall comply with this Section.

(b)	WGRs that are part of an SGIA signed prior to November 1, 2008 are not required to meet this Section.  However, individual WGRs that are newly installed or replaced shall be VRT capable in accordance with the VRT requirements of this Section.

(c)	Notwithstanding any of the foregoing provisions, VRT capability of IRRs shall be maintained or improved over time.

(d)	IRRs shall provide a status of compliance to ERCOT System Planning upon request.

(2)	IRRs are required to set generator voltage relays to remain in-service during all transmission faults (no more than nine cycles) and to allow the system to recover in accordance with Figure 1, Default Voltage Ride-Through Boundaries For IRRs, below.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary then generator voltage relays are required to be set to remain connected and recover in accordance with Figure 1.

(3)	IRRs shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of nine cycles as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(4)	IRRs may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(5)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(6)	If the IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries For IRRs. The default clearing period is nine cycles or 0.15 seconds. Recovery time to +/-10% of per unit voltage should be within 105 cycles, or 1.75 seconds. IRRs should not trip for system voltages within the boundary