## Slide 1: PDCWG Report to ROS
August 11, 2011
Sydney Niemeyer

## Slide 2: In This Report
Recent Improvement in Primary Frequency Response.
High Frequency Event July 15, 2011.
Short Supply conditions and Primary Frequency Response.
ERCOT Frequency Control Performance – May, June & July.
PDCWG On-going work.

## Slide 4: Improved Reliability

## Slide 10: Great Accomplishment!
The PDCWG would like to thank the ERCOT Compliance group and their effort in working with the Market Participants in a positive effort.
The PDCWG would like to thank the generators for their effort in improving their performance.

## Slide 11: High Frequency Event
July 15, 2011

## Slide 12
ERCOT System went down. When returning to service, SCED calculated ~4000 additional MW in the form of 5 minute Base Points that were dispatched to QSE’s. Frequency went to 60.109 Hz.

## Slide 13: Business Practice Manual
ERCOT And QSE Operations Practices During The Operating Hour. Section 3 states:
  Additionally, the ERCOT LFC system provides for each On-Line Generation Resource an Updated Desired Base Point (UDBP) in the telemetry data set. The UDBP is a calculated MW value representing the expected MW output of a Generation Resource ramping between successive SCED Base Points. The QSE is expected to control each of its Generation Resources to follow the UDBP and additionally if the Generation Resource is assigned Regulation AS Resource Responsibility it must follow UDBP plus net Regulation deployment,

## Slide 14: Protocols
Base Point Deviation measures Resource performance to the average 5 Minute Base Points during the 15 minute period.
GREDP measures Resource performance to the average 5 Minute Base Points during the 5 minute period.

## Slide 15: How QSE’s Implemented Resource Control defines their Response during this event.
When frequency exceeds a threshold, the UDBP will freeze if its direction contributes to the frequency error.
16 QSE’s followed the UDBP and provided Primary Frequency Response to stabilize frequency. Most dropped output during the event. (PFR > than the up change in UDBP).
14 QSE’s followed the 5 minute Base Points and contributed to the high frequency.
4 QSE’s did not receive upward Base Points but did not provide Primary Frequency Response to the high frequency.

## Slide 16: Consistent and Clear Instructions Needed
If the Base Point Deviation calculation included a Primary Frequency Response obligation and followed the UDBP, the correct behavior would be incentivized.
Reliability would improve.

## Slide 17: PDCWG Work on Review of RRS and Frequency Responsive Reserves
At the July 5th, 6th and August 3rd PDCWG meeting, work continued on the holistic review of frequency responsive reserves in ERCOT.

## Slide 18: Primary Frequency Response During Short Supply Conditions
Responsive Reserve Ancillary Service Capacity on Generators and Load Dampening can be the only source of Primary Frequency Response for extended periods of time.
  Frequency sensitivity will be greater during electrical energy and mechanical energy imbalances as frequency stabilizes.
    Summer Peak Load Dampening can be as high as -166 MW/0.1 Hz
    Winter Peak Load dampening will be less, -73 MW/0.1 Hz, due to higher percent of resistive load.
    Additional PFR from RRS Generators will provide an additional -191 MW/0.1 Hz.

## Slide 19
Recent Operation During EEA Step 2A and 2B Emphasizes An Important Difference
Regulation Up Service was fully deployed.
Load Resources fully deployed.
SCED Up Capacity was limited to the capacity of un-deployed Responsive Reserve Service from Generators.

## Slide 20: ERCOT Frequency Control Performance
May, June and July, 2011

## Slide 37: PDCWG On-going Work
Participating in the NERC BAL-003 Primary Frequency Response Field Trial.
  Frequency Response performance to be submitted to NERC by August 15 for all frequency events since Dec 1, 2010.
NERC Reliability Metrics Working Group and the measurement of Interconnection Primary Frequency Response.
  Frequency Response performance to be submitted to NERC by Sept 1, 2010 for all frequency events since Dec 1, 2009 to present using a continent wide standard measurement process.
PDCWG next meeting is August 31, 2011

## Slide 38
Questions?