| NOGRR Number | 069 | NOGRR Title | Relay Misoperation Reporting Changes for Consistency with ERO-RAPA Proposal |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Tabled |
| Date of Decision |  | June 16, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Sections Requiring Revision |  | 6.2.1, Introduction 6.2.3, Performance Analysis Requirements for ERCOT System Facilities 8, Attachment B, Relay Misoperation Report |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) updates ERCOT’s requirements for relay misoperation reporting in order to be consistent with the North American Electric Reliability Corporation’s (NERC’s) ERO-RAPA proposal for quarterly reporting. Changes to Section 6.2.3 govern the events that qualify as a relay misoperation while the changes to Section 8, Attachment B, govern what data must be submitted in the event of a relay misoperation. This NOGRR also revises the definition of protective relay systems for consistency with NERC and to correct an erroneous use of Direct Current Tie (DC Tie). |  |  |
| Reason for Revision |  | This NOGRR updates ERCOT relay misoperation reporting requirements to be consistent with other NERC regions. |  |  |
| Overall Market Benefit |  | This NOGRR will provide ERCOT the ability to be consistent with other NERC regions in terms of relay misoperation reporting. This NOGRR will allow NERC to produce the ALR4-1 metric “Automatic Transmission Outages Caused by Protection System Misoperations” on a consistent basis. |  |  |
| Overall Market Impact |  | Relay misoperation reporting will change from an annual requirement to a quarterly requirement. Although most data fields remain the same, some of the data fields submitted as part of the quarterly requirement will change from what is in place for the existing annual requirement. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 4/6/11, NOGRR069 was posted. - On 4/7/11, CenterPoint Energy comments were posted. - On 4/7/11, the motion to grant NOGRR069 Urgent status passed via ROS e-mail vote. - On 4/11/11, Texas Reliability Entity (Texas RE) comments were posted. - On 4/11/11, ROS considered NOGRR069. - On 5/5/11, System Protection Working Group (SPWG) comments were posted. - On 5/12/11, ROS again considered NOGRR069. - On 5/26/11, an Impact Analysis was posted. - On 6/1/11, a second set of SPWG comments were posted. - On 6/2/11, TAC considered NOGRR069. - On 6/16/11, ROS again considered NOGRR069. |  |  |
| ROS Decision |  | On 4/11/11, ROS unanimously voted to table NOGRR069 and to refer the issue to the System Protection Working Group (SPWG). All Market Segments were present for the vote. On 5/12/11, ROS voted to recommend approval of NOGRR069 as amended by the 5/5/11 SPWG comments as revised by ROS. There were three abstentions from the Independent Generator, Independent Retail Electric Provider (IREP) and Investor Owned Utility (IOU) Market Segments. All Market Segments were present for the vote. On 6/16/11, ROS unanimously voted to table NOGRR069. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 4/11/11, the 4/11/11 Texas RE comments were discussed. It was noted that a letter released by NERC in late 2010 requires quarterly reporting of relay misoperations regardless of the Nodal Operating Guide language, which currently requires an annual report. The degree to which the Nodal Operating Guide requirements need to conform to NERC requirements was discussed. It was requested that the SPWG review the NERC checklist to determine if reporting for other types of misoperations should be required by the Nodal Operating Guides. On 5/12/11, it was noted that the SPWG considered the 4/11/11 Texas RE comments. There was concern expressed that the definition for “Failure to Trip” as written could be misinterpreted to mean that a misoperation occurred if backup relay does not clear. It was noted that the guide language should be clarified to state that both the reach and time characteristics are included in the zone of protection of a protective relay system. Whether the relay misoperation requirements should be imposed on all Facility owners or just Transmission Facility owners was also discussed. On 6/16/11, Market Participants were urged to attend a meeting of interested parties scheduled for June 29, 2011 to resolve outstanding issues. |  |  |
| TAC Decision |  | On 6/2/11, TAC unanimously voted to remand NOGRR069 to ROS. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 6/2/11, concern was expressed regarding redundant requirements in NOGRR069, and it was requested that TAC remand NOGRR069 to ROS to for further review. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | ERCOT should be consistent with NERC’s ERO-RAPA proposal. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Relay misoperation reporting database field updates. | <$2,000 per Market Participant, one-time cost due to database re-design requirements. |
|  | 2 | Reporting will move from an annual basis to a quarterly basis. | <$1,000 per Market Participant, first year cost due to transition to new requirements, training, etc. |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Relay misoperation prevention due to enhanced focus on relay misoperation events. | $1,000 per occurrence, ongoing benefit due to avoided outages and a reduced number of repeated misoperations. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | More consistent, frequent, and improved relay misoperation event analysis. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | A guide has been developed by the SPWG to map existing relay misoperation database fields to the new fields outlined in Section 8, Attachment B, to ease the transition to the new format. |  |
|  | 2 | Moving from annual to quarterly reporting for relay misoperations may yield productivity benefits associated with performing that task on a more frequent basis and not having to review a full year’s worth of data each time. |  |
|  | 3 | Resources have been added to paragraph (2) of Section 6.2.3. |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Kris Koellner on behalf of the SPWG |
| E-mail Address | kristian.koellner@lcra.org |
| Company | LCRA |
| Phone Number | (512) 369-4573 |
| Cell Number |  |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| CenterPoint Energy 040711 | Proposed revisions to better align the reporting requirements with the NERC misoperation reporting template. |
| Texas RE 041111 | Addressed importance of consistency with ERO-RAPA proposal and proposed corresponding revisions. |
| SPWG 050511 | Proposed clarifying language changes and introduced Section 6.2.1 to correct an erroneous use of DC Tie. |
| SPWG 060111 | Proposed revisions to clarify what constitutes a reportable event. |

Proposed Guide Language Revision

- 6.2.1	Introduction

(1)	The satisfactory operation of the ERCOT System (equipment operated above 60 kV), especially under abnormal conditions, is greatly influenced by protective relay systems.  Protective relay systems are defined as the total combination of:

(a)	The protective relays;

(b)	Associated communications system;

(c)	Voltage and current sensing devices; and

(d)	The station DC supply associated with protective functions (including batteries, battery chargers, and control circuitry).

- (2)	Although relaying of tie points between facility owners is of primary concern to the ERCOT System, internal protective relay systems often directly, or indirectly, affects the adjacent area also.  Facility owners are those Entities owning facilities in the ERCOT System.  Facility owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  Protective relay systems of individual facility owners shall not adversely affect the stability of ERCOT System interconnections.  Additional minimum protective relay system requirements are outlined in the North American Electric Reliability Corporation (NERC) Reliability Standards.

- 6.2.3	Performance Analysis Requirements for ERCOT System Facilities

(1)	All ERCOT System disturbances (unwanted trips, faults, and protective relay system operations and automatic reclosing operations) shall be analyzed by the affected Facility owner(s) promptly and any deficiencies shall be investigated and corrected.

(2)	All protective relay system and automatic reclosing misoperations in Resource systems and Transmission Facility systems 100 kV and above shall be documented, including corrective actions and the documentation supplied by the affected Facility owner(s) to ERCOT or NERC upon their request within five Business Days.  All protective relay system and automatic reclosing misoperations shall be documented quarterly using the format in Section 8, Attachment B, Protection System Misoperation Report.  Any of the following events constitute a reportable protective relay system or automatic reclosing misoperation:

(a)	Failure to Trip – Any failure of a protective relay system to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device (zone of protection includes both the reach and time characteristics);

(b)	Slow Trip – A correct operation of a protective relay system for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intends;

(c)	Unnecessary Trip During a Fault – Any initiated operation of a circuit breaker during a fault when the fault is outside the intended zone of protection

(d)	Unnecessary Trip Other Than Fault – The unintentional operation of a protective relay system, which causes a circuit breaker to trip when no system fault is present.  May be due to vibration, improper settings; load swing, defective relays, or SCADA system malfunction;

(e)	–Facility owner authorized personnel action that directly initiates a trip is not included in this category.  It is the intent of this reporting process to identify misoperations of the protective relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the protective relay system.  If an individual directly initiates an operation, it is not counted as a misoperation (i.e., unintentional operation during tests); however, if a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a protective relay system misoperation.

(f)	Failure to Reclose – Any failure of a protective relay system or automatic reclosing to automatically reclose following a fault if that is the system design intent.

(3)	All SPS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five Business Days.  SPS misoperations shall be included in the quarterly misoperations report requirements.  All SPS misoperations shall be documented using the format in Section 8, Attachment B.  Any of the following events constitute a reportable SPS misoperation:

(a)	Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occur;

(b)	Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed;

(c)	Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s);

(d)	Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s); and

(e)	Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the system design intent.

(4)	Facility owners shall document the performance of their protective relay systems utilizing the method described in the paper “Transmission Protective Relay System Performance Measuring Methodology,” IEEE/PSRC Working Group I3 September 16, 1999.  The performance data reported shall include the total number of protective relay system and automatic reclosing misoperations, the total number of events, and the factor “k.”

(5)	Reporting of protective relay system and automatic reclosing misoperations shall be submitted to the Texas Reliability Entity (TRE) on a quarterly basis per the following schedule:

| Data submission | Date |
| --- | --- |
| Submission of the 1st Quarter data | May 31 |
| Submission of the 2nd Quarter data | August 31 |
| Submission of the 3rd Quarter data | November 30 |
| Submission of the 4th Quarter data and IEEE Protective Relay System Performance summary | February 28 |

(6)	At least annually, ROS designated working groups shall review the protective relay system and automatic reclosing misoperation reports and, at least annually, 345 kV performance data of Facility owners for analysis of protective relay system and automatic reclosing performance.

(6)	All Facility owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in Section 6.1.2.3, Data Recording Requirements.

(7)	Facility owners shall provide an assessment of the system performance results of simulation tests of the contingencies as required by NERC Reliability Standards.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Reliability Standards and the associated Table I.  All non-compliance findings shall be documented per NERC requirements, including a plan for achieving compliance.  These assessments shall be provided to NERC or ERCOT upon their request within 30 days of the request.

Section 8, Attachment B, Protection System Misoperation Report

- Protection System Misoperation Report

Protective relay system and automatic reclosing misoperations shall be reported in the format requested by the Texas Reliability Entity (TRE).  As a minimum, all fields of data specified in the table below shall be included in the report.  The file shall include the "Field Names" listed in the table below as headers for each field and the data size/format shall match "Size and/or Format" specified in the table below.

Each row in the Protection System Misoperation Report records one misoperation. If an event has more than one misoperation associated with it, there should be more than one row reported that pertains to the event. In a multi-misoperation event, information from one misoperation can be copied or repeated in another misoperation associated with the same event, if appropriate. In this case, providing the Transmission Availability Data System (TADS) event code identifies that each misoperation was associated with a single event.

| Field Name | Type | Size and/or Format | Description |
| --- | --- | --- | --- |
| - Resubmittal Check | Text | Drop down | NERC reporting requirements include quarterly reporting. Individual misoperation entries may require review and updates that bridge the quarterly reporting requirements. To capture metrics properly notification of resubmittal is required. Default is No. |
| - Regional Entity | Text | Drop down | Name of Regional Entity |
| - Entity Name | Text | 25 characters | Name of Entity (NERC Registration Name) |
| - Misoperation Date | Date | mm/dd/yyyy | The date of the misoperation. |
| - Misoperation Time | Time | hh:mm:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| - Time zone | Text | Drop down | Define the standard time zone of the misoperation time noted (i.e. CST, EST, etc.) |
| - Facility Name (Location of misoperation) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify the name of the facility (i.e., substation or generating station) where the misoperation occurred. |
| - Equipment Name (protected by Protection System that Misoperated) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify by name the generator, transmission line, transformer, bus or equipment protected by the Protection System that Misoperated. |
| - Equipment Type | Text | Drop down | Select type of equipment being protected ( e.g., Line, Transformer, etc.) from drop-down list |
| - Facility Voltage | Text | Drop down | Select system voltage (in kV) of the protected element (if transformer, high side kV) from drop-down list. |
| - Equipment Removed from Service | Text | 32,767, utilizing Names used in Network Operations Model per TAC approved naming convention | Enter names of the equipment becoming unavailable due to the event (Equipment only refers to circuits, transformers, busses, but not breakers UNLESS the breaker is the only element). |
| - Event Description | Text | 32,767 | Provide a brief description of the event and detailed description of misoperation root causes (see cause code in Column N). |
| - Misoperation Category | Text | Drop down | Select Misoperation Category from drop-down list. |
| - Cause(s) of misoperation | Text | Drop down | Select root cause(s) of the misoperation from drop-down list. Detailed definitions of the root causes are provided. |
| - Protection Systems/Components that Misoperated | Text | 32,767 | Only provide information on the components/protective relay systems that misoperated. If misoperated components are relays, list relay models (types) and protection schemes. |
| - Relay Technology | Text | Drop down | Select Electromechanical, Solid State, or Micro Processor from drop-down list |
| - Is this a TADS reportable outage? | Text | Automated | This field is automatically populated based on Voltage selection. No manual entry is needed. |
| - Corresponding TADS Cause Code | Text | Automated | This field is automatically populated to show the corresponding TADS cause code(s). No manual entry is needed. |
| - Enter one or more TADS "Event IDs" if this is a TADS reportable outage? | Text | 32,767 | Create a TADS Event ID using TADS Form 5 |
| - Analysis and Corrective Action Status | Text | Drop down | Select the status from drop-down list. In general, misoperation analysis is conducted first, and then a Corrective Action Plan will be developed and implemented to mitigate the misoperation. |
| - Corrective Action Plan | Text | 32,767 | Identify the corrective action(s). |
| - Corrective Action Plan Target Completion Date | Date | mm/dd/yyyy | If corrective actions are not complete, estimate when they will be complete. |
| - Actual Completion Date | Date | mm/dd/yyyy | If corrective actions are complete, enter actual completion date. |
| - Reported By | Text | 25 | Enter the name of the person filling out the report. |
| - Phone | Text | 50 | Enter the reporting person’s phone number. |
| - E-Mail | Text | 50 | Enter the reporting person’s E-MAIL address. |
| - Date Reported | Date | mm/dd/yyyy | Enter the report date. |

| Causes(s) of Misoperation |  |
| --- | --- |
| AC system | This category includes misoperations due to problems in the ac inputs to the protective relay system. Examples would include misoperations associated with CT saturation, loss of potential, or rodent damaged wiring in voltage or current circuit. |
| As-left personnel error | This category includes misoperations due to the as-left condition of the protective relay system following maintenance or construction procedures. These include test switches left open, wiring errors not associated with incorrect drawings, carrier grounds left in place, or settings placed in the wrong relay, or incorrect field settings left in the relay that do not match engineering approved settings. |
| Communication failures | This category includes misoperations due to failures in the communication systems associated with protection schemes inclusive of transmitters and receivers. Examples would include misoperations caused by loss of carrier, spurious transfer trips associated with noise, Telco errors resulting in malperformance of communications over leased lines, loss of fiber optic communication equipment, or microwave problems associated with weather conditions. |
| DC system | This category includes misoperations due to problems in the DC control circuits. These include problems in the battery or charging systems, trip wiring to breakers, or loss of dc power to a relay or communication device. |
| Incorrect setting/logic/design errors | This category includes misoperations due to “engineering” errors by the protective relay system owner. These include setting errors, errors in documentation, and errors in application. Examples would include uncoordinated settings, incorrect schematics, or multiple CT grounds in the design. |
| Relay failures/malfunctions | This category includes misoperations due to improper operation of the relays themselves. These may be due to component failures, physical damage to a device, firmware problems, or manufacturer errors. Examples would include misoperations caused by changes in relay characteristic due to capacitor aging, misfiring thyristors, damage due to water from a leaking roof, relay power supply failure, or internal wiring/logic error. Failures of auxiliary tripping relays fall under this category. |
| Unknown/unexplainable | Requires extensive documentation of investigative actions if this cause code is utilized. |