| NOGRR Number | 069 | NOGRR Title | Relay Misoperation Reporting Changes for Consistency with ERO-RAPA Proposal |
| --- | --- | --- | --- |
| Date Posted |  | April 6, 2011 |  |

| Nodal Operating Guide Sections Requiring Revision | Section 6.2.3, Performance Analysis Requirements for ERCOT System Facilities Section 8, Attachment B, Relay Misoperation Report |
| --- | --- |
| Protocol Section(s) Requiring Revision, if any | None. |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) | Urgent. ERCOT must update relay misoperation reporting requirements to be consistent with the North American Electric Reliability Corporation’s (NERC’s) ERO-RAPA (Reliability Assessment and Performance Analysis) proposal for quarterly reporting starting in 2011. Q1 2011 data is due May 31, 2011. This proposal was communicated to each NERC region on October 12, 2010. |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) updates ERCOT’s requirements for relay misoperation reporting in order to be consistent with NERC’s ERO-RAPA proposal for quarterly reporting. Changes to Section 6.2.3 govern the events that qualify as a relay misoperation while the changes to Section 8, Attachment B, govern what data must be submitted in the event of a relay misoperation. |
| Reason for Revision | This NOGRR updates ERCOT relay misoperation reporting requirements to be consistent with other NERC regions. |
| Overall Market Benefit | This NOGRR will provide ERCOT the ability to be consistent with other NERC regions in terms of relay misoperation reporting. This NOGRR will allow NERC to produce the ALR4-1 metric “Automatic Transmission Outages Caused by Protection System Misoperations” on a consistent basis. |
| Overall Market Impact | Relay misoperation reporting will change from an annual requirement to a quarterly requirement. Although most data fields remain the same, some of the data fields submitted as part of the quarterly requirement will change from what is in place for the existing annual requirement. |
| Consumer Impact | None. |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | ERCOT should be consistent with NERC’s ERO-RAPA proposal |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Relay misoperation reporting database field updates. | <$2,000 per Market Participant, onetime cost due to database re-design requirements |
|  | 2 | Reporting will move from an annual basis to a quarterly basis. | <$1,000 per Market Participant, first year cost due to transition to new requirements, training, etc. |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Relay misoperation prevention due to enhanced focus on relay misoperation events. | $1,000 per occurrence, ongoing benefit due to avoided outages and a reduced number of repeated misoperations |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | More consistent, frequent, and improved relay misoperation event analysis. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | A guide has been developed by the System Protection Working Group (SPWG) to map existing relay misoperation database fields to the new fields outlined in Section 8, Attachment B, to ease the transition to the new format. |  |
|  | 2 | Moving from annual to quarterly reporting for relay misoperations may yield productivity benefits associated with performing that task on a more frequent basis and not having to review a full year’s worth of data each time. |  |
|  | 3 | As written, this NOGRR will remove the existing requirement to report “failure to reclose” events as a misoperation. Removing this requirement is consistent with NERC’s ERO-RAPA proposal regarding what qualifies as a relay misoperation. |  |
|  | 4 | As written, this NOGRR will remove the existing requirement to use the Institute of Electrical and Electronic Engineers (IEEE) “Transmission Protective Relay System Performance Measuring Methodology”. Removing this requirement has been done because “failure to reclose” is included as part of this methodology. Also, NERC does not require this methodology to be used as part of the ERO-RAPA proposal. |  |

| Sponsor |  |
| --- | --- |
| Name | Kris Koellner on behalf of the System Protection Working Group (SPWG) |
| E-mail Address | kristian.koellner@lcra.org |
| Company | LCRA |
| Phone Number | (512) 369-4573 |
| Cell Number |  |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

Proposed Guide Language Revision

- 6.2.3	Performance Analysis Requirements for ERCOT System Facilities

(1)	All ERCOT System disturbances (unwanted trips, faults, and protective relay system operations) shall be analyzed by the affected Facility owner(s) promptly and any deficiencies shall be investigated and corrected.

(2)	All protective relay system misoperations in systems 100 kV and above shall be documented, including corrective actions and the documentation supplied by the affected Facility owner(s) to ERCOT or NERC upon their request within five Business Days.  All protective relay system misoperations shall be documented using the form in Section 8, Attachment B, Relay Misoperation Report.  Any of the following events constitute a reportable protective relay system misoperation:

(a)	Failure to Trip – Any failure of a protective relay system element to operate when a fault or abnormal condition occurs within a zone of protection.  Note that lack of targeting, such as when a high-speed pilot system is beat out by high-speed zone, is not a reportable misoperation.  Furthermore, if the fault clearing is consistent with the time normally expected with proper functioning of at least one protection system, then a primary or backup protection system failure to operate is not required to be reported.

(b)	Slow Trip – Any failure of a protective relay system element that is slower than planned to operate when a fault or abnormal condition occurs within the zone of protection.  When a high-speed protective relay system is employed but is not essential for transmission system performance, the failure of the high-speed system is not required to be reported if fault clearing is consistent with correct operation of a backup protective relay system with an intentional time delay

(c)	Unnecessary Trip During a Fault – Any unnecessary protective relay system operation for a fault not within the zone of protection.  Note that operation as backup protection for a fault in an adjacent zone that is not cleared within the specified time for the protection for that adjacent zone is not a reportable misoperation.

(d)	Unnecessary Trip Other Than Fault – Any unnecessary protective relay system operation when no fault or other abnormal condition has occurred.  Note that an operation that occurs during on-site maintenance, testing, construction and/or commissioning activities is not a reportable misoperation.

(3)	Additional clarification regarding protective relay system misoperations:

(a)	Trip Initiated by a Control System - Operations which are initiated by control systems (not by protective relay system), such as those associated with generator controls, or turbine/boiler controls, circuit breaker mechanism, or other facility control systems, are not misoperations.

(b)	Trip Initiated by a Facility Owner Employee - Employee action that directly initiates a trip is not included in this category.  It is the intent of this reporting process to identify misoperations of the relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the relay system.  If an individual directly initiates an operation, it is not counted as a misoperation (i.e., unintentional operation during tests); however,If a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a relay system misoperation.

(c)	Failure of Relay Communications – A communication failure in and of itself is not a misoperation if it does not result in misoperation of the associated protective relay system

(4)	All SPS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five Business Days.  All SPS misoperations shall be documented using the format in Section 8, Attachment B.  Any of the following events constitute a reportable SPS misoperation:

(a)	Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occur;

(b)	Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed;

(c)	Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s);

(d)	Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s); and

(e)	Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the design intent.

(5)	At least annually, ROS designated working groups shall review the protective relay system misoperation reports and 345 kV performance data of Facility owners for analysis of protective relay system performance and compliance.

(6)	All facility owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in Section 6.1.2.3, Data Recording Requirements.

(7)	Facility owners shall provide an assessment of the system performance results of simulation tests of the contingencies as required by NERC Reliability Standards.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Reliability Standards and the associated Table I.  All non-compliance findings shall be documented, including a plan for achieving compliance.  These assessments shall be provided to NERC or ERCOT upon their request within 30 days of the request.

Section 8, Attachment B, Relay Misoperation Report

- Relay Misoperation Report

Relay misoperations shall be reported in the format requested by the Texas Regional Entity (TRE).  All fields of data specified in the table below shall be included in the report.  The file shall include the "Field Names" listed in the table below as headers for each field and the data size/format shall match "Size and/or Format" specified in the table below.

Each row in the Relay Misoperation Report records one misoperation. If an event has more than one misoperation associated with it, there should be more than one row reported that pertains to the event. In a multi-misoperation event, information from one misoperation can be copied or repeated in another misoperation associated with the same event. In this case, providing the TADS event code identifies that each misoperation was associated with a single event.

| Field Name | Type | Size and/or Format | Description |
| --- | --- | --- | --- |
| - Resubmittal Check | Text | Drop down | New NERC reporting requirements include quarterly reporting. Individual misoperation entries may require review and updates that bridge the quarterly reporting requirements. To capture metrics properly double notification of resubmittal is required. Default is No. |
| - Regional Entity | Text | Drop down | Name of Regional Entity |
| - Entity Name | Text | 25 characters | Name of Entity |
| - Misoperation Date | Date | mm/dd/yyyy | The date of the misoperation. |
| - Misoperation Time | Time | hh:mm:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| - Time zone | Text | Drop down | Define the standard time of the misoperation time noted (i.e. CST, EST, etc.) |
| - Facility Name (Location of misoperation) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify the name of the facility (i.e., substation or generating station) where the misoperation occurred. |
| - Equipment Name (protected by Protection System that Misoperated) | Text | Name used in Network Operations Model per TAC approved naming convention | Identify by name the generator, transmission line, transformer, bus or equipment protected by the Protection System that Misoperated. |
| - Equipment Type | Text | Drop down | Select type of equipment being protected ( e.g., Line, Transformer, etc.) from drop-down list |
| - Facility Voltage | Text | Drop down | Select system voltage (in kV) of the protected element (if transformer, high side kV) from drop-down list. |
| - Equipment Removed from Service | Text | 255, utilizing Names used in Network Operations Model per TAC approved naming convention | Enter names of the equipment becoming unavailable due to the event (Equipment only refers to circuits, transformers, busses, but not breakers UNLESS the breaker is the only element). |
| - Event Description | Text | 255 | Provide a brief description of the event and detailed description of misoperation root causes (see cause code in Column P). |
| - Protection System Components that Misoperated | Text | 255 | Only provide information on the components/protection systems that misoperated. If misoperated components are relays, list relay models (types) and protection schemes. |
| - Relay Technology | Text | Drop down | Select Electromechanical, Solid State, or Micro Processor from drop-down list |
| - Misoperation Category | Text | Drop down | Select Misoperation Category from drop-down list. |
| - Cause(s) of misoperation | Text | Drop down | Select root cause(s) of the misoperation from drop-down list. Detailed definitions of the root causes are provided below. |
| - Is this a TADS reportable outage? | Text | Drop down | Select Yes or No from drop-down list. |
| - Corresponding TADS Cause Code | Text | Automated | This field is automatically populated to show the corresponding TADS cause code(s). No manual entry is needed. |
| - Enter one or more TADS "Event IDs" if this is a TADS reportable outage? | Text | 255 | Create a TADS Event ID using TADS Form 5 (Typically, a TADS Event does not last for more than 5-10 minutes. If a misoperation lasts for 30 minutes or more, there will likely be more than one TADS Event ID to be entered in this column. The TADS Form 5 "Event IDs" can be entered by the TO (or his delegated reporting entity; i.e. TOP or relay technician) at any time of the day or night. TADS is always running . . .for those Users who wish to do partial data entry on the same day as the Event) |
| - Analysis and Corrective Action Status | Text | Drop down | Select the status from drop-down list. In general, misoperation analysis is conducted first, and then a Corrective Action Plan will be developed and implemented to mitigate the misoperation. |
| - Corrective Action Plan | Text | 255 | Identify the corrective action(s). |
| - Corrective Action Plan Target Completion Date | Date | mm/dd/yyyy | If corrective actions are not complete, estimate when they will be complete. |
| - Actual Completion Date | Date | mm/dd/yyyy | If corrective actions are complete, enter actual completion date. |
| - Reported By | Text | 25 | Enter the name of the person filling out the report. |
| - Phone | Text | 50 | Enter the reporting person’s phone number. |
| - E-Mail | Text | 50 | Enter the reporting person’s E-MAIL address. |
| - Date Reported | Date | mm/dd/yyyy | Enter the report date. |

| Causes(s) of Misoperation |  |
| --- | --- |
| AC system | This category includes misoperations due to problems in the ac inputs to the protection system. Examples would include misoperations associated with CT saturation, loss of potential, or rodent damaged wiring in voltage or current circuit. |
| As-left personnel error | This category includes misoperations due to the as-left condition of the protection system following maintenance or construction procedures. These include test switches left open, wiring errors not associated with incorrect drawings, carrier grounds left in place, or settings placed in the wrong relay, or incorrect field settings left in the relay that do not match engineering approved settings. |
| Communication failures | This category includes misoperations due to failures in the communication systems associated with protection schemes inclusive of transmitters and receivers. Examples would include misoperations caused by loss of carrier, spurious transfer trips associated with noise, Telco errors resulting in malperformance of communications over leased lines, loss of fiber optic communication equipment, or microwave problems associated with weather conditions. |
| DC system | This category includes misoperations due to problems in the DC control circuits. These include problems in the battery or charging systems, trip wiring to breakers, or loss of dc power to a relay or communication device. |
| Incorrect setting/logic/design errors | This category includes misoperations due to “engineering” errors by the protection system owner. These include setting errors, errors in documentation, and errors in application. Examples would include uncoordinated settings, incorrect schematics, or multiple CT grounds in the design. |
| Relay failures/malfunctions | This category includes misoperations due to improper operation of the relays themselves. These may be due to component failures, physical damage to a device, firmware problems, or manufacturer errors. Examples would include misoperations caused by changes in relay characteristic due to capacitor aging, misfiring thyristors, damage due to water from a leaking roof, relay power supply failure, or internal wiring/logic error. Failures of auxiliary tripping relays fall under this category. |
| Unknown/unexplainable | Requires extensive documentation of investigative actions if this cause code is utilized. |