## Slide 1: Joint PLWG/CMWG Assignment Update to ROS
August 11, 2011
Notes: 07/28/26
<number>

## Slide 2
<number>
Joint CMWG/PLWG Assignment
May 17 Board Resolution:
THEREFORE be it RESOLVED, that the ERCOT Board hereby approves the revised ERCOT Business Practice, Setting the Shadow Price Caps and Power Balance Penalties in Security Constrained Economic Dispatch, as described in Attachment A to be effective on May 25, 2011, and directs the Technical Advisory Committee (TAC) to report back to the ERCOT Board on the following: (1) a recommendation for a holistic methodology for setting appropriate Shadow Price caps for constraints not resolvable by Security Constrained Economic Dispatch (SCED) and (2) a recommendation for addressing gaps between operations and planning processes to be able to
identify constraints not resolvable by SCED.
This presentation incorporates a high level summary of concepts shown in the Luminant presentation from the June 14, 2011 Joint CMWG/PLWG Meeting. The presentation is available on the ERCOT Calendar for this meeting at: http://www.ercot.com/calendar/2011/06/20110614-CMWG
Notes: 07/28/26
<number>

## Slide 3
<number>
2008 Planning Case Load Level for 2011 ~ 74,500 MW
50 Hours SCED Irresolvable
High Load Conditions: 58,000 – 64,000 MW (~255 Hours)**
~50 Hours of SCED Irresolvable Constraints (19.5% of hours)
$40 Million Congestion during these hours
* Includes 1,500 MW of LAAR and EILS deployment ** Load data from 12/1/10 – 7/31/11
2008 View of Expected Summer 2011 Load Level
Actual operating conditions stress the transmission system significantly more than what is seen in the current planning models as evidenced by the frequent occurrence of SCED Irresolvable congestion. Through July 2011, nearly 20% of all intervals during which the load was 58,000 MW or higher, had at least one SCED Irresolvable Constraint active.
~ 67,000MW *

## Slide 4
<number>
41 Transmission facilities with post-contingency overloads.
EEA Event:
Contingencies were shown as “inactive”, although there were no SPSs or switching solutions (e.g. RAPs) available. This assists ERCOT Operations by making all capacity available to achieving power balance and operating reserves.
August 4, 2011 @15:47, ERCOT ~67,000 MW

## Slide 5
<number>
SCED Irresolvable Constraint History
Protocol 6.5.7.1.10 (3): If the SCED does not resolve an insecure state, ERCOT shall attempt to relieve the insecure state by …..

## Slide 6
<number>
Application of Planning Criteria
Nodal Operating Guide Section 5.3 (2): The contingency studies will be performed for reasonable variations of Load level, generation schedules, planned transmission line Maintenance Outages, and anticipated power transfers.
Question: What is a “reasonable variation”?
TSPs report that in practice, transmission planning studies include various sensitivities; however, there are two dominant concerns.

## Slide 7
<number>
Concern1:
A proposed transmission project based on assumptions that are materially different than the base case:
  Is less likely to be endorsed by ERCOT
  Will require a commitment of scarce resources to prove-out validity of assumptions
  May not be the best use of scarce resources
Consideration:
Predetermine A Permissive Set of “Reasonable” Assumptions:
  ERCOT determine and maintain 90% percentile outcomes of temperature driven load, thermal generation unavailability, and summer dynamic line ratings (using CRR case methodology).
  The project submitter may use these variations knowing that ERCOT and Market Participants have already accepted these assumptions as “reasonable”.
  ERCOT is tasked to post and maintain this data on the POI website.

## Slide 8
<number>
Concern 2:
Is it appropriate to “stack” multiple adverse conditions concurrently?
  90th percentile load,
  90th percentile generator outage/derate,
  90th percentile peak temp driven dynamic line ratings
  Up Ancillary Services (RRS, Reg Up, and potentially NSRS)
Isn’t the joint probability of these conditions occurring simultaneously low?
Consideration:
Historical outcomes indicates that simultaneous multiple stressful conditions are not unusual, and are often highly correlated.
Extreme temperatures correlated to:
  Extreme high load
  Higher thermal generation unavailability
  Summer dynamic line ratings that may be below nominal ratings
Operational history has demonstrated this repeatedly:
  February 2nd-4th, 2011
  April 17th, 2006
  August 3rd, 2011, etc…
Up Ancillary Services are always required by ERCOT for reliability
  Must not be double counted as available for cong. management unless ERCOT Operations has provisions in for their use for that purpose

## Slide 9
<number>
A “best case” study, without applying condition variations, can produce a contingency load level of as low as 80%.
Applying assumptions consistent with stressful operating conditions reveal a probable overload.
Actual July Performance:
Congestion: $3.4M over 19.5 hours (reached SCED irresolvable)
SCED irresolvable:
  Load ~53,500 MW
  NZ & WZ Wind 66MW
  Cond. rating ~1,126 MVA (static = 1,072)
A
B
DFW Imports Southeast of Dallas
If “reasonable variations” are limited to “one generator out”, study will indicate contingency loading of 80% after system adjustments. July operating conditions show a post contingency loading of up to 112.5% with some*, but not all, of the stressful conditions shown above.
* Some West Zone NSRS on-line and generating, Dynamic line rating > static rating…..
July 2011 saw 32 hours with a contingency overload of up to 112.5% on this line

## Slide 10
<number>
Operations vs Planning Consistency Approach
Modify Planning Criteria to clarify and explicitly allow the project submitter to apply modeling assumptions as summarized below.

## Slide 11
<number>
Next Steps to Meet October Board Meeting Deadline:
August 4: PGRR submitted by Luminant Energy
August 11: Seeking ROS Urgency declaration for PGRR
August 12: Further review & discuss in joint CMWG/PLWG meeting
September 15: Seek ROS Approval of PGRR
October 6: Seek TAC Approval of PGRR
October 18: Seek Board Approval of PGRR
On August 4, Luminant submitted a PGRR with language that provides the clarifications and additions as described on the previous slide.