| NOGRR Number | 076 | NOGRR Title | Synchronization with NPRR298 and New Format for Black Start Plans |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | August 17, 2011 |  |  |
| Proposed Effective Date |  | November 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Sections Requiring Revision |  | 1.4, Definitions 1.5.1, System Operator Training Objectives 2.3, Ancillary Services 4.3, Operation to Maintain Transmission System Security 4.5.2, Operating Procedures 4.6, Black Start Service 4.6.1, Principles 4.6.2, Strategies 4.6.3, Priorities 4.6.4, Responsibilities 4.6.5, Black Start Emergency Back Up Communication Facilities Criteria 8, Attachment A, Detailed Black Start Information 8, Attachment E, Black Start Plan Template (New) |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR): - Synchronizes the Nodal Operating Guides with Nodal Protocol Revision Request (NPRR) 298, New Definitions Related to Black Start and Clarification to the Hourly Standby Fee Payments for Black Start Resources (formerly “New Definitions Related to Black Start”), which introduced new black start terminology and corrected the acronym related to the Hourly Standby Fee Payment. NPRR298 was approved by the ERCOT Board on April 19, 2011. - Introduces new black start terminology to the Nodal Operating Guides; - Creates a requirement for all Transmission Operators (TOs) to submit their black start plans to ERCOT by November 1 of each year; and - Introduces a template for black start plans to the Nodal Operating Guides. |  |  |
| Reason for Revision |  | This NOGRR synchronizes the Nodal Operating Guides with NPRR298 and clarifies the processes and terminology currently used for restoration of the ERCOT System. Additionally, a black start plan template is necessary so that all TOs provide the information necessary for ERCOT to develop its black start plan. |  |  |
| Overall Market Benefit |  | A standardized format of TO black start plans provided to ERCOT. This standardized format is also beneficial in that it will allow other Market Participants to share information more quickly. |  |  |
| Overall Market Impact |  | None. Black start plans are currently submitted on an annual basis. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 7/5/11, NOGRR076 was posted. - On 7/20/11, the Operations Working Group (OWG) considered NOGRR076. - On 8/5/11, an Impact Analysis was posted. - On 8/17/11, OWG considered the 7/20/11 OWG Report and Impact Analysis for NOGRR076. |  |  |
| OWG Decision |  | On 7/20/11, the OWG was in consensus to recommend approval of NOGRR076 as revised by OWG. On 8/17/11, the OWG was in consensus to endorse and forward the 7/20/11 OWG Report as revised by OWG and Impact Analysis for NOGRR076 to ROS. |  |  |
| Summary of OWG Discussion |  | On 7/20/11, it was noted that NOGRR076 introduces a requirement for all black start plans to be submitted by November 1 of each year; that since NOGRR076 will not be implemented until November 1, 2011, a Market Notice will be sent in October requesting black start plans be submitted by November 1, 2011; that all black start plans should be submitted using the template in new Section 8, Attachment E; that ERCOT should report testing activities to ROS by April 1 of each year; that the Black Start Working Group (BSWG) should develop a test template for the annual report to ROS; and that ERCOT will review paragraph (1)(d) of Section 4.6.4 and submit comments to clarify the language if necessary. On 8/17/11, ERCOT Staff stated that in addition to annual submission of TO black start plans, TOs should submit an update to plans at a minimum, on a biannual basis, or 45 days after a system topology change occurs that impacts the TO’s black start plan and procedures. Participants were concerned that the proposed change is in conflict with a requirement in Section 9.4.2, Black Start Service Requirements for TSPs, QSEs, and Generation Resources, and agreed that a new NOGRR should be submitted to address the conflict. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | A standardized format of TO black start plans provided to ERCOT. This standardized format is also beneficial in that it will allow other Market Participants to share information more quickly. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Steve Zaragoza on behalf of the BSWG |
| E-mail Address | stevez@gplops.org |
| Company | Garland Power and Light |
| Phone Number | 972.205.3098 |
| Cell Number |  |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512.248.4513 |

Proposed Guide Language Revision

1.4 	Definitions

Cranking Path

A set of elements in the system that establishes an electrical path from a contracted Black Start Resource to a designated next start Resource.

Intercompany Connections

The connection between two or more independent transmission companies.

Intra-Company

Occurring within or between the branches of a single company.

Island

An electrically separated portion of the ERCOT System with independent frequency, generation and Load.

Synchronization Corridors

A predetermined section of the ERCOT Transmission Grid that may be utilized to synchronize Islands after a Partial Blackout or ERCOT Blackout.

- 1.5.1	System Operator Training Objectives

(1)	Each operating Entity within the ERCOT System shall train its operators such that they will possess the necessary knowledge, skills and abilities to perform their assigned tasks in directing the operation of the bulk power system.  Instruction provided shall be in accordance with North American Electric Reliability Corporation (NERC) Reliability Standards, the Protocols, these Operating Guides, and ERCOT Procedures, as well as individual Entity operating goals, plans and procedures.

(2)	Training will prepare operators to:

(a)	Maintain the safety of personnel, even during emergency situations involving complex switching and manipulation of control elements;

(b)	Protect system components, particularly major power system elements from serious life degradation or harm;

(c)	Operate the system in a secure manner to minimize violations of operating limits, avoiding customer Outages where reasonably possible, and avoiding unstable situations that might result in widespread Outages or Partial Blackout or Blackouts;

(d)	Operate the system using Good Utility Practices whenever possible within continually changing operating environment; and

(e)	Restore the system to its normal operating state as rapidly as practical after a disturbance.

- 2.3	Ancillary Services

The types of Ancillary Services required by ERCOT are described below:

| ANCILLARY SERVICE TYPE | DESCRIPTION | ERCOT AUTHORITY ACTION |
| --- | --- | --- |
| Regulation Down Service (Reg-Down) and Regulation Up Service (Reg-Up) (for Generation Resources) Reference: Protocol Section 2, Definitions and Acronyms | Resource capacity provided by a Qualified Scheduling Entity (QSE) from a specific Resource to control frequency within the system which is controlled second by second, normally by an Automatic Generation Control (AGC) System. | a. Reg-Down energy is a deployment to increase or decrease generation at a level below the Resource’s base point in response to a change in system frequency. b. Reg-Up energy is a deployment to increase or decrease generation at a level above the Resource’s base point in response to a change in system frequency. |
| Reg-Down and Reg-Up (for Load Resource) Reference: Protocol Section 2, Definitions and Acronyms | Load Resource capacity provided by a QSE from a specific Load Resource to control frequency within the system. | a. Reg-Down is a deployment to increase or decrease Load as deployed within its Ancillary Service Schedule for Reg-Down below the Load Resource’s Maximum Power Consumption (MPC) limit in response to a change in system frequency. b. Reg-Up is a deployment to increase or decrease Load as deployed within its Ancillary Service Schedule for Reg-Up above the Low Power Consumption (LPC) limit in response to a change in system frequency. |
| Responsive Reserve (RRS) Service Reference: Protocol Section 2, Definitions and Acronyms | Operating reserves on Generation Resources and Load Resources maintained by ERCOT to help control the frequency of the system. RRS on Generation Resources and controllable Load Resources that are qualified to provide regulation can also be used as a backup regulation service and energy during an Energy Emergency Alert (EEA) event. | RRS may only be deployed as follows: a. Through automatic governor action or under-frequency relay in response to frequency deviations; b. By electronic signal from ERCOT in response to the need; and c. As ordered by an ERCOT Operator during EEA or other emergencies. |
| Non-Spinning Reserve (Non-Spin) Service Reference: Protocol Section 2, Definitions and Acronyms | a. Off-Line Generation Resource capacity, or reserved capacity from On-Line Generation Resources, capable of being ramped to a specified output level within 30 minutes, and operating at a specified output for at least one hour b. Load Resources that are capable of being interrupted within 30 minutes and remaining interrupted for at least one hour. | Deployed in response to loss-of-Resource contingencies, Load forecasting error, or other contingency events on the system. As described in Protocol Section 6.5.7.6.2.3, Non-Spinning Reserve Service Deployment. |
| Voltage Support Service (VSS) Reference: Protocol Section 3.15, Voltage Support | Reactive capability of a Generation Resource that is required to maintain transmission and distribution voltages on the ERCOT Transmission Grid within acceptable limits. All Generation Resources with a gross rating greater than 20 MVA shall provide VSS. | Direct the scheduling of VSS by providing Voltage Profiles at the point of interconnection. The Generation Resource is obligated to maintain the published voltage profile within its Corrected Unit Reactive Limit (CURL). |
| Black Start Service Reference: Protocol Section 3.14.2, Black Start | The provision of Generation Resources under a Black Start Agreement, which are capable of self-starting without support from within ERCOT in the event of a Partial Blackout or Blackout. | Provide emergency Dispatch Instructions to begin restoration to a secure operating state after a total or Partial Blackout or Blackout. |
| Reliability Must-Run (RMR) Service Reference: Protocol Section 3.14.1, Reliability Must Run | The provision of Generation Resource capacity and energy under an RMR Agreement. | Enter into contractual agreements to retain units required for reliable operations. Direct the operation of those units that otherwise would not operate and that are necessary to provide reliable operations. |

- 4.3	Operation to Maintain Transmission System Security

(1)	ERCOT Operators are responsible for operating the ERCOT System within “First Contingency” (N-1) transfer limits so that there is no overload of any significant Transmission Element whose loss could jeopardize the reliability of the ERCOT System.  Whenever the ERCOT System is not engaged in emergency operation, it will be operated in such a manner that the occurrence of a Credible Single Contingency will not cause any of the following:

(a)	Uncontrolled breakup of the transmission system;

(b)	Loading of Transmission Facilities above defined Emergency Ratings which can not be eliminated in time to prevent damage or failure following the loss through execution of specific, predefined operating procedures;

(c)	Transmission voltage levels outside system design limits which can not be corrected through execution of specific, predefined operating procedures before voltage instability or collapse occurs; or

(d)	Customer Outages, except for high set interruptible and radially served loads.

(2)	Significant Transmission Overload – ERCOT can:

(a)	Order adjustment to unit generation schedules, switching of Transmission Elements or Load interruption to relieve a severely overloaded Transmission Element;

(b)	Order a Transmission Element whose loss would not have a significant impact on the reliability of transmission system switched out to increase interconnected system transfers.

(3)	Violation of “First Contingency” (N-1) Criteria – ERCOT can order changes to unit dispatch or commitment to eliminate a “First Contingency” (N-1) criteria violation.  Normally these changes should be performed via the market control mechanisms of constraint management as described in the Protocols, but ERCOT Operators have the authority to issue Verbal Dispatch Instructions (VDIs) independent of these systems.

(4)	Violation of Voltage/Reactive Criteria – ERCOT can order changes in unit dispatch if coordinated voltage and Reactive Power criteria that are considered critical to interconnection reliability are violated for the existing or “Contingency” (N-1) conditions.

(5)	Partial Blackout or Blackout – ERCOT shall implement Black Start procedures.

- 4.5.2	Operating Procedures

(1)	The ERCOT System Operators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions.  ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a Partial Blackout or Blackout.  These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service.  Transmission Service Providers (TSPs) will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting Load, notifying others and restoration of service.

(2)	ERCOT and each TSP will endeavor to maintain transmission ties intact if at all possible.  This will:

(a) 	Permit rendering the maximum assistance to an area experiencing a deficiency in generation;

(b) 	Minimize the possibility of cascading loss to other parts of the system; and

(c) 	Assist in restoring operation to normal.

(3)	ERCOT's operating procedures will meet the following goals while continuing to respect the confidentiality of market sensitive data.  If all goals cannot be respected simultaneously then the priority order listed below shall be respected:

(a)	Maintain station service for nuclear generating facilities;

(b)	Securing startup power for power generating plants;

(c)	Operating generating plants isolated from ERCOT without communication;

(d)	Restoration of service to critical Loads such as:

(i)	Military facilities;

(ii)	Facilities necessary to restore the electric utility system;

(iii)	Law enforcement organizations and facilities affecting public health; and

(iv)	Communication facilities

(e)	Maximum utilization of ERCOT System capability;

(f)	Utilization of Responsive Reserve (RRS) services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(g)	Utilization of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT System; and

(h)	Restoration of service to all Customers following major system disturbances, giving priority to the larger group of Customers.

4.6	Black Start Service

(1)	This section provides general guidelines to be followed in the event of a Partial Blackout or Blackout of the ERCOT System.  Timely implementation of a restoration plan compiled according to these Operating Guides should facilitate coordination between ERCOT, Qualified Scheduling Entities (QSEs) who represent Black Start Resources, and Transmission Operators (TOs) and ensure restoration of service to the ERCOT System at the earliest possible time.  Those QSEs representing contracted Black Start Resources will provide ERCOT with the individual plant start-up procedures for coordination of their activities with those of the appropriate TO.

(2)	Pre-established plans and procedures cannot foresee all the possible combinations of system problems that may occur after a major failure.  It is the responsibility of ERCOT to restore the system to normal, applying the principles, strategies, and priorities outlined in the ERCOT Black Start Plan.

- 4.6.1	Principles

(1)	In order to minimize the time required, ERCOT will develop the Black Start Plan to utilize the principles, strategies, and priorities outlined in this Guide.  The ERCOT Black Start Plan shall be coordinated with local TO Black Start plans, to provide a coordinated Black Start reference.

(2)	Each contracted Black Start Resource and each QSE with contracted Black Start Resource(s) will have readily accessible and sufficiently detailed current operating procedures to assist in an orderly recovery.

(3)	Mutual assistance and cooperation will be essential during the restoration.  Deliberate, careful action by each QSE, TO, and Resource Entity is necessary to minimize the length of time required for restoration and to avoid the reoccurrence of a Partial Blackout or Blackout of the ERCOT System.

(4)	Throughout the restoration, recovery will depend on ERCOT receiving an accurate assessment of system conditions and status from each QSE, TO, and Resource Entity throughout the restoration.  Adequate and reliable communications must be available within the ERCOT System.  During Black Start recovery, communication restrictions may enable the sharing of market sensitive information that pertains to the restoration of the ERCOT System.  This includes but is not limited to availability status and recovery activities.

- 4.6.2	Strategies

In the event of a Partial Blackout or Blackout of the ERCOT System, immediate steps must be taken to return the interconnected network to normal as quickly as possible.  For detailed Black Start information, refer to Section 8, Attachment A, Detailed Black Start Information.

(1)	Each TO shall immediately initiate its portion of the ERCOT Black Start Plan and attempt to establish contact with ERCOT.  If communications with ERCOT are unavailable the TO shall immediately establish communications with its interconnected Black Start Resource(s) and the Black Start Resource’s QSE.

(2)	Each QSE who represent Black Start Resources shall initiate communications with its Black Start Resources and immediately notify ERCOT and the appropriate TO of their condition and status.

(3)	Available Black Start Resources shall immediately start their isolation and startup procedures and attempt to establish communications with the local TO.

(4)	As generating and transmission capabilities become available, systematic restoration of ERCOT Load with respect to priorities shall begin in accordance with the local TO Black Start plans, taking care to balance Load and generating capability while maintaining an acceptable frequency.

(5)	Appropriate voltage levels and reactive control must be maintained during the restoration.  Consideration should be given to connecting Islands at locations having communications, frequency control, voltage control, synchronization facilities, and adequate transmission capacity.  ERCOT will coordinate the return to full Automatic Generation Control (AGC) in the interconnection.

- 4.6.3	Priorities

Priorities for an ERCOT System Black Start recovery are listed below:

(1)	Secure and/or stabilize generating units where necessary.

(2)	Prepare Cranking Paths and Synchronization Corridors as necessary to support restoration.

(3)	Assess ERCOT System condition, and available communication facilities.

(4)	Restore and maintain communication facilities to the extent possible.

(5)	Bring units with contracted Black Start capability On-Line.

(6)	Provide service to critical facilities:

(a)	Provide station service for nuclear generating facilities;

(b)	Provide critical power to as many Generation Resources as possible to prevent equipment damage;

(c)	Secure or provide startup power for Generation Resources that do not have Black Start capability; and

(d)	Supply station service to critical substations where necessary.

(7)	Connect Islands at designated synchronization points taking care to avoid recurrence of a Partial Blackout or Blackout of the ERCOT System.

(8)	Restore service to critical Loads such as:

(a)	Military facilities;

(b)	Facilities necessary to restore the electric utility system, including fuel sources;

(c)	Law enforcement organizations and facilities affecting public health; and

(d)	Public communication facilities.

(9)	Restore service to the remaining Customers.  Attention should be given to restoring feeders with under-frequency relay protection.

- 4.6.4	Responsibilities

(1)	ERCOT’s responsibilities are as follows:

(a)	Shall maintain a Black Start plan in accordance with NERC Reliability Standards;

(b)	Coordinate and approve Planned Outage schedules for contracted Black Start Generation Resources;

(c)	Train QSE, TO, Resource Entity, and Market Participant personnel in the restoration of the ERCOT System.  This training will cover the theory of restoration and the processes that will need to be implemented during a Partial Blackout or Blackout;

(d) 	Will review the plans and procedures for consistency and conformance with these Operating Guides and ensure that they are updated at least annually;

(e) 	ERCOT shall report to the Reliability and Operations Subcommittee (ROS) by April 1 of each year a plan for review and any testing activities of Black Start Generation Resources;

(f) 	Shall verify that the number, size, and location of system Black Start Generation Resources are sufficient to meet system restoration plan expectations; and

(g)	In the event of a Partial Blackout or Blackout of the ERCOT System, ERCOT will:

(i)	Maintain continuous surveillance of the status of the ERCOT System;

(ii)	Act as a central information collection and dissemination point for the ERCOT Region;

(iii)	Coordinate reconnection of transmission;

(iv)	Direct assistance for QSEs who represent Black Start Resources, TOs, Resource Entities, and Market Participants;

(v)	Direct the distribution of reserves;

(vi)	Coordinate the return of the ERCOT System to AGC.

(2)	TOs’ responsibilities are as follows:

(a)	Shall submit their Black Start Plans to ERCOT by November 1 of each year via secured webmail or encrypted data transfer; and

(b)	In event of a Partial Blackout or Blackout of the ERCOT System:

(i)	Shall communicate with local Black Start Resources and the Black Start unit’s QSE;

(ii)	Coordinate switching to next start Resources and local Load;

(iii)	Shall implement its local Black Start plan;

(iv)	Shall follow the direction of ERCOT on behalf of represented TSPs and DSPs;

(v)	Shall act as the regional ERCOT representative in coordinating interconnection of Resources; and

(vi)	Shall follow the direction of ERCOT for reconnection of islands.

(3)	QSEs’ (representing Black Start Resources) responsibilities are as follows:

(a)	Verify that associated personnel are proficient in its implementation and use of the QSE Black Start Resource Black Start Plan; and

(b)	In the event of a Partial Blackout or Blackout of the ERCOT System, the QSEs representing Black Start Resources shall:

(i)	Take immediate steps to initiate the local Black Start plan;

(ii)	Supply ERCOT and/or the local TO with information on the status of generation, fuel, transmission, and communication facilities;

(iii)	Follow the direction of the local TO or ERCOT in picking up local Load and starting next units; and

(iv)	Provide available assistance as directed by ERCOT or the local TO.

(4)	Section 8, Attachment A, Detailed Black Start Information, provides a detailed and specific Black Start information guide.  Interested parties should use this information for technical reference material, Black Start testing, development of Black Start plans, and training of personnel.

- 4.6.5	Black Start Emergency Back Up Communication Facilities Criteria

(1)	All back-up communications systems shall meet the following minimum requirements:

(a)	Be operational for 72 hours immediately following the start of a Blackout of the ERCOT System without external power from the ERCOT System;

(b)	Provide direct voice communications between Black Start Resource and TO, TO and other appropriate TOs, and TO and ERCOT; and

(c)	Maintain written procedures that address operator training and the testing of the communication system;

(2)	TOs shall have a satellite phone that meets the minimum back up communication requirements as a back-up communication system and that is compatible with ERCOT’s satellite phone.

# Section 8, attachment A, Detailed Black Start Information

- Section 8A and 8E, Black Start Plan Template, provide the minimum information necessary to be used in conjunction with the ERCOT Black Start Plan.  Each Transmission Operator (TO), Qualified Scheduling Entity (QSE) with Black Start Resources, and Black Start Generation Resource should use this information for technical reference, development of Black Start Plans, and training of personnel.

# CONSIDERATIONS FOR SYSTEM RESTORATION

## Determining System Status

(1)	If a Generation Resource or Transmission Operator (TO) loses voltage on all busses and incoming transmission lines, then operators should assume there is a Partial Blackout or Blackout.  If possible, the TO shall also immediately notify ERCOT.  Contracted Black Start Resources shall implement Black Start procedures and establish contact with their TOs.  Other Generation Resources shall contact their QSEs and then wait for instructions from the TOs.  If possible, ERCOT will update TOs and QSEs concerning the status of the ERCOT System by use of the ERCOT Hotline or other available backup communications.

(2)	It is expected that if communication with ERCOT is not possible, TOs will evaluate system conditions and proceed independently with their Black Start Plans.

(3)	Priority should be given to determining the status of nuclear Generation Resource and switchyards in order to re-establish offsite power supply.

(4)	System status conditions to be surveyed include but are not limited to:

(a)	Areas of the system that are de-energized;

(b)	Areas of the system that are functioning;

(c)	Amount of generating reserve available in functioning areas;

(d)	 Generation Resource availability and time required to restart;

(e)	Status of transmission breakers and sectionalizing equipment along Cranking Paths and Synchronization Corridors, and at Generation Resources;

(f)	Status of transmission breakers and sectionalizing equipment at Direct Current Ties (DC Ties);

(g)	Status of fuel supply from external suppliers;

(h)	Under-frequency relay operation; and

(i)	Relay flags associated with circuits tripped by protective relays.

## Verifying Communications

(1)	Reliable communications will be the key to a safe and timely restoration following a Partial Blackout or Blackout.  As part of the initial assessment after a Partial Blackout or Blackout, communication facilities shall be tested and verified.  It is possible, especially in case of a Blackout, that communications with out-of-state QSEs representing Generation Resources may not be possible.  It is therefore critical that TOs and Generation Resources located within their transmission system be able to communicate directly during these times.

- (a)	The ERCOT System Operators shall:

(i)	Verify or establish communication paths with TOs;

(ii)	Verify or establish communications paths with QSEs representing Generation Resources;

(iii)	Verify integrity of ERCOT Hotline;

(iv)	Periodically disseminate information to TOs and QSEs; and

(v)	Direct implementation of Black Start Plan in areas of a Partial Blackout or Blackout.

- (b)	The TO operators shall:

(i)	Contact ERCOT in order to report status;

(ii)	Establish contact with contracted Black Start Resources and their QSE(s);

(iii)	Initiate Black Start Plan; and

(iv)	Establish communication paths with other Generation Resources necessary to the restoration of the ERCOT System.

(c)	The QSE representing Resources shall:

(i)	Contact ERCOT to report status of Generation Resources within the ERCOT  Region;

(ii)	Assist TOs as required; and

(iii)	Ensure Generation Resources are prepared to receive and follow instructions directly from the TO to which they are connected.

(d)	The Black Start Resources shall:

(i)	Isolate their Black Start Resource from the ERCOT Transmission Grid;

(ii)	Establish communications with their TOs;

(iii)	If no communications with the TOs are available, establish communications with ERCOT; and

(iv)	Start Black Start Resource and request load interconnection from TO.  The Black Start Resource shall not connect to the ERCOT Transmission Grid without specific instructions to do so from either ERCOT or the designated TO responsible for the Black Start Resource.

- (2)	Should problems be encountered with any of the primary communication facilities, back-up facilities shall be deployed and appropriate personnel notified.

- (3)	Communications will be vital to an orderly recovery.  To keep communication facilities available, operating personnel shall ensure that  three part communication is used at all times.

- Preparing for System Restoration

(1)	Orderly restoration will usually require sectionalizing the de-energized parts of the ERCOT System into smaller, manageable blocks before they are energized.

(2)	The sectionalizing process should usually address but is not limited to the following objectives:

(a)	Priority shall be given to restoring offsite power to nuclear Generation Resources s;

(b)	Ensure that blocks of load to be energized are sized to minimize the problems of cold load pickup; and

(c)	Operators shall verify that their switching orders as well as any standing emergency switching orders have been completed.

- Bringing Up Generation Resources

(1)	First priority shall be given to preventing damage to Generation Resource  equipment and to restoring offsite power to nuclear  Generation Resources.  Secondly, attention shall be given to preparing generators that can come On-Line most rapidly.  All operators should remember that large steam Generation Resources  will need an outlet for the minimum generation requirement soon after coming On-Line.

(2)	A Black Start Generation Resource  has procedures to begin the process of bringing its generators back up when the switchyard and all incoming transmission lines are de-energized.  The Generation Resource  shall not synchronize or pick up load without communicating with the TO to which it is connected.

(3)	A Generation Resource  without black start capability shall have a written procedure in place to begin preparing the Generation Resource  to be energized from an external line.  When the TO has energized the Generation Resource  switchyard it will contact the Generation Resource directly and the QSE as soon as practical.  The TO will coordinate starting of large motors, bringing Generation Resources on line, and synchronizing Generation Resources  with the rest of the  ERCOT Transmission Grid.

(4)	Generation Resource  operators will be controlling system frequency during the recovery period and must keep it between trip points for generator’s under-frequency and over-frequency relays.  It is preferable to use the generators with lowest under-speed trip for initial restoration.

(5)	Automatic Voltage Regulators (AVRs) should be placed in service as soon as practical after bringing Generators  On-Line and should remain in service to improve machine stability.

(6)	As soon as possible, after bringing a Generator  On-Line, automatic Governor controls should be placed in the "automatic" position to ensure instantaneous Governor response to changes in frequency.

- Picking Up Lines

(1)	Ties between nearby Generation Resources  shall be established as soon as possible.  Priority shall be given to restoring at least one circuit to nuclear Generation Resources  to provide offsite power for safe shutdown.

(2)	A line should be energized from the strongest electrical source.  Switching devices on all substation or transmission capacitor banks along the line should be open unless needed for voltage control.

(3)	Energizing transmission auto-transformers (345/138 kV, 138/69 kV) and shunt reactors at Generation Resources will allow plant operators to increase field current on the generator to increase stability.  Also, this reactive current will help keep transmission voltages from becoming excessive.

(4)	Caution should be exercised in the use of 345 kV transmission system.  Because of high values of line charging, energizing one of these circuits with little or no load can produce excessive voltage and can damage substation equipment  (Note: 345kV lines supply approximately 1 MVAR/mile of line charging while 138kV lines supply approximately 0.1 MVAR/mile).

(5)	Operators in TO control rooms should exercise care when energizing transmission lines, so that they do not close a breaker into a fault.  Operators in TO control rooms should be aware of any transmission lines that tripped while the system was going down and have field personnel check the relay flags before energizing the line.

(6)	Ferroresonance may occur while energizing a line or while picking up a transformer from an unloaded line.  Operators in TO control rooms should be on guard for unusually high and sustained voltages during such switching.  345 kV lines may be highly susceptible to this phenomenon and their use should be minimized in the early stages of restoration.

(7)	Impedance relays that do not have out of step blocking may trip lines due to power swings during restoration (a good indication that the line tripped due to excessive power swings rather than a fault is the existence of impedance relay flags and no ground flags).

## Picking Up Load

(1)	In general, 69 kV and 138 kV lines along with radial 345 kV lines to autotransformers may be used to energize load.  When energizing a 345 kV circuit and autotransformer combination, both the line and transformer should be energized at the same time to avoid the problem of excessive voltage.  The more lightly loaded a generator is, the less load increment it can safely pick up.

(2)	Cold load pick up can involve inrush currents of ten or more times than the normal load current depending on the nature of the load being picked up.  This will generally decay to about two times the normal load current in two to four seconds and remain at a level of 150% to 200% of pre-shutdown levels for as long as 30 minutes.

(3)	Priority shall be given to restoring offsite power to nuclear  Generation Resources.  As critical and priority loads are restored, consideration should be given to restoration of loads controlled by under-frequency relays.

(4)	When energizing load, the operators in TO control rooms must be in close contact with the Generation Resource in order that excessive load is not picked up on a generator in one operation.  Generally, the operators in TO control rooms should pick up no more than 5% of the total generating capability in an Island in a single step.  If load is picked up in blocks that are too large, then the inrush current may operate over current relays that trip the loads off the ERCOT System again.  There should be sufficient time between switching operations to allow the generator to recover from the sudden increase in load.

(5)	The operators in TO control rooms should exercise caution when loading a single generator to more than 50% of its control range until additional generators have been brought back on-line in that island. Generally, no generator should be loaded to more than 80% of its available capability until ERCOT System conditions return to normal.

(6)	Since each Generation Resource may be operating independently, Generation Resource  operators will have to monitor and adjust their generators voltage and frequency.  Frequency should be kept above 59.8 Hz and as close as possible to 60 Hz.  Voltage should be kept as close as possible to normal schedules.  As more generators are brought up and more load is added, the voltage and frequency will tend to stabilize.

(7)	Residential and commercial load will most likely be easier to pick up and maintain than industrial loads.  This is due to the large fluctuation possible with industrial loads.

(8)	The operators in TO control rooms should exercise caution when re-energizing capacitor banks after load has been picked up.  The change in system voltage that occurs will be much larger than normal because of the reduced system fault duty.

- Synchronizing Between Islands

(1)	TOs shall have field personnel in area Islands to check breakers at each end of a line being used to synchronize between Islands to ensure they are open regardless of supervisory indication.  The area with the largest amount of generation On-Line shall energize the line first.

(2)	Where available, field personnel shall synchronize and close the tie breakers at the synchronization point.  If there is a sufficient frequency difference that the Islands cannot be synchronized, the Island with the least generation On-Line shall adjust its frequency to achieve synchronization.

(3)	When synchronizing, both the phase angle across the breaker, and the voltage on each side of the breaker shall be measured.  If possible, the phase rotation should be stopped and the phase angle reduced to 10° or less before closing the breakers.

(4)	In general, lines should not be loaded to more than 50% of thermal rating until multiple tie paths have been established.  Additional ties should be closed as soon as possible.

- ERCOT Coordination

(1)	During the initial stages of the restoration ERCOT will coordinate the black start restoration effort by monitoring the implementation of each TO’s Black Start Plan, providing ERCOT System status information, and facilitating communication between the Market Participants.  ERCOT will also monitor the changes in  Resource conditions, restoration of transmission lines, and any load that is re-energized.  The ERCOT Hotline or available backup communications will periodically be used to communicate simultaneously with the Market Participants on a periodic basis assuming communication is possible.

(2)	System status conditions that should be surveyed include, but are not limited to:

- (a)	Communication facilities;

- (b)	Transmission system;

- (c)	Generating system;

- (d)	Fuel supplies; and

(e)	Any other significant conditions which might affect restoration

- (3)	ERCOT System Operators should be sure that each TO is successfully implementing their Black Start Plan and each Generation Resource is successfully implementing their written procedures for preparing their Generation Resources to be energized during black start restoration.  ERCOT System Operators will direct mutual assistance by utilizing the black start map and contacting the Market Participants most able to provide the assistance.

(4)	Before synchronization of Inter-company Islands ERCOT will designate the entity responsible for frequency control in the combined Islands.  Initially this may be a single Generation Resource.  As the restoration effort progresses, ERCOT will work to combine Islands in such a way as to restore frequency control of one of the QSEs representing Generation Resources.  As Inter-company Islands are synchronized ERCOT will approve the addition of generation and load to the ERCOT System.  No additions shall be made without that approval.

- Considerations for Black Start Testing

(1)	ERCOT shall maintain a record of contracted Black Start  Resources and update such records on an annual basis.  The record shall include the name, location, MW capability, type of unit, date of test, and starting method of each Black Start Resource per the North American Electric Reliability Corporation (NERC) Reliability Standards.

- (2)	The owner or operator of each Black Start Resource shall demonstrate through the testing procedures outlined in Protocol Section 8.1.1.2.1.5, System Black Start Capability Qualification, that the Black Start Resource can perform its intended functions as required in the ERCOT Black Start Plan.  ERCOT may also order random simulation or testing of black start capabilities. Documentation of the analysis shall be provided to NERC or the reliability monitor upon request as required by the NERC Reliability Standards.

- Criteria for ERCOT and Transmission Operator Black Start Plans

(1)	ERCOT will maintain a Black Start Plan that is consistent with this Operating Guide.  The ERCOT Black Start Plan shall be provided to the QSEs representing Black Start Resources, TOs..

(2)	ERCOT System Operators shall review these documents on a regular basis.  It is suggested that all Black Start Plans include at a minimum the following elements:

- (a)	Strategies and guidelines for restoration of the ERCOT System.

- (b)	Identification of the relationships and responsibilities of the QSEs who represent Black Start  Resources and TO personnel necessary for the restoration.

- (c)	Identification of Black Start Resources including:

- (i)	Generation Resources.

- (ii)	Transmission Facilities.

- (iii)	Communication resources.

- (iv)	Fuel resources.

- (d)	Mutual assistance arrangements.

- (e)	Contingency plans for failed Generation Resources.

- (f)	Identification of critical load requirements

- (g)	Identification of special equipment requirements

- (h)	General instructions and guidelines for ERCOT System Operators, Resource Entity, QSEs who represent Generation Resources, and TO operators and their respective communications personnel.

- (i)	Procedures for Notification.

(j)	Procedures for return to Market Operations.

(3)	Transmission Operator’s (TO’s)  Black Start Plans shall include sections on the Black Start Purpose, Scope, Roles and Responsibilities, Strategies, Priorities, Operations, Communication, and Contingency plans and shall follow the format outlined Appendix 8E, Black Start Plan Template.

ERCOT Nodal Operating Guides

Section 8

Attachment E, Black Start Plan Template

month day, year

- This attachment provides a template to be used by each Transmission Operator (TO) and Qualified Scheduling Entity (QSE) who represents Black Start Resources for the development of their Black Start Plans.  Pursuant to Protocols, all TOs and QSEs who represent Black Start Resources are required to submit their Black Start Plan to ERCOT.

- Black Start Plan Template

- Purpose - The Purpose Statement will address the intended outcome of the TOs Black Start Plan

- Scope - A Scope statement shall be incorporated in the TO Black Start Plan.  The Scope statement shall provide, in a brief summary, the boundaries of the plan and to whom the plan applies.

- Definitions: Definitions of terms that are used in the TO and ERCOT Black Start Plan that are not common to the ERCOT Region

- Roles and Responsibilities – Identify the TO’s role as well as those Generation Resources and ERCOT in case of a Partial Blackout or Blackout.

  - Key Personnel

    - System Operations – List of personnel responsible for coordinating in emergency and system restoration (i.e., chief system operator, directors, managers)

    - Generation Resources – List of personnel responsible for the operation of Black Start Resource (i.e. manager, shift supervisors)

    - Generation Control (Qualified Scheduling Entities (QSE) – List of personnel responsible for managing Black Start Resources)

  - Key Personnel Contact List – List of phone numbers, e-mail address, etc.

- Strategies

  - General Considerations – General considerations to include ERCOT System conditions (voltage and frequency control, availability of Resources, Outages, etc).

- Priorities

  - Identifying the Blackout event - Clearly state how a blackout event will be recognized and identify actions the TO needs to perform in order to initiate restoration as well as actions that should be expected from ERCOT and other Market Participants.

  - Assessing and verifying communication capabilities - Include a procedure for assessing communication capabilities and a plan for dealing with failures of various systems.

  - Transferring control away from ERCOT - Acknowledge that, in the event of a Blackout, the TO will have ERCOT’s authority to bring Generation Resources on line and energize Load.  The TO should note that it may not be possible for ERCOT to communicate this transfer of authority and that the transfer can be assumed, once a blackout condition has been identified.

  - Starting the Black Start Generation Resources- Primarily rely on contracted Black Start Generation Resources in restoring the ERCOT System.  However, the TO Black Start Plan should also account for non-contracted Black Start Resource capabilities and, if possible, incorporate these resources.

  - Building stable Island(s) - Primarily focus on building stable islands with the ultimate goal of reaching synchronization points.  TO plans should also consider that while larger islands are more stable they might be more difficult to synchronize with neighboring islands.

  - Reaching synchronization points - Focus on restoring the system and not restoring service to customers.  The primary focus of the TO plan should be on building a stable island that reaches a designated synchronization point.

  - Synchronizing islands - Instruct operators to contact ERCOT when islands are ready to be synchronized.  Actual synchronization will occur with TOs communicating directly with each other.  ERCOT will coordinate frequency control.  For Intra-Company islands the plan should contain instructions for adding Load and Generation Resources.

  - Restoring load after synchronization - Note that after synchronization occurs between islands, ERCOT will direct the further addition of Load and Generation Resources.  The TO will continue to add Load, but it will be at the direction of ERCOT as specified in the Strategy section of this plan.

- Operations – The TO Black Start Plan should address at least the following items and include subsection for operations of each island.

  - Generation (Contracted Black Start Resource):

    - Blackout Recognition – The process a Black Start Resource operator would use to recognize a Partial Blackout or Blackout.

    - System Status Verification – The process a Black Start Resource operator would use to determine status of the transmission system.

    - General Guidelines

      - Fuel Source and Alternate Fuel Source

      - Fuel Switching

    - Generation Partial Blackout or Blackout Procedures

      - Restoration of station service to non-Black Start Resources

      - Non-contracted black start Resources

        - Contact Information

        - Start-up Characteristics

        - Load Pick-Up Procedures

        - Next Start Resources Contact Information

        - Start-up Characteristics

        - Load Pick-Up Procedures

        - Co-Generation / Private Use Networks

  - Transmission

- Blackout Recognition - The process a TO would use to recognize a Partial Blackout or Blackout.

- System Status Verification - The process a TO would use to determine system status including condition of Black Start Resources.

- Verification Of Tie Line Status

- Black Start Corridors

- Switching Guidelines - an overall switching philosophy including special considerations or procedures for switching of transmission belonging to another TO.

- Cranking Paths – Switching guidelines for Cranking Paths from a Black Start Resource to the designated next start Resource including a one-line diagram

- Primary Synchronization Corridors – Switching guidelines for Primary Synchronization corridor include a one-line diagram.

- Secondary Synchronization Corridors – Switching guidelines for secondary synchronization corridor including a one-line diagram.

- Breakers with Synchronization Capability

- Location and ownership of each synchronization point.

- Synchronization procedures and special requirements for each location.

- Communication with ERCOT

- Coordinated Restoration Efforts

- Transmission Line Considerations – Special considerations given for system equipment that falls outside the normal mode of operation.

- Relay Action Considerations

- Intercompany Connection Considerations

- Black Start Island Connection

- Load Restoration

- Priorities (Critical Loads)

- System Voltage and Frequency Consideration

  - Communications

- Overview of Telecommunication System

- Communication Requirements

- Mobile Radio Considerations

- Telephone System Considerations

- Satellite Phone Considerations

- Backup Power Supplies

- Failure of Critical Communications

- Backup Power Supplies

- Failure of Primary Telephone Voice Communication

- Failure of Radio System

  - Contingency Plan

- Black Start Secondary Corridors

- Failure of Contracted Black Start Resources

- Failure of Contracted Black Start Resources to Start Next Star Resources

- Emergency Power Supply

- Control Center Power Supplies

- Backup Control Center Supplies

- Loss of Substation Battery