| NPRR Number | 389 | NPRR Title | Modification of Voltage Support Requirements to Address Existing Non-Exempt WGRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | August 18, 2011 |  |  |
| Proposed Effective Date |  | November 1, 2011 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 3.15, Voltage Support |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) clearly defines the Reactive Power capability requirements for Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (Existing Non-Exempt WGRs). These Existing Non-Exempt WGRs will fall into two categories: - Those whose current design allows them to meet the Reactive Power capability requirement described in paragraph (3) of Section 3.15. In these cases, the Reactive Power profile is depicted graphically as a rectangle. - Those whose current design does not allow them to meet the Reactive Power capability requirement described in paragraph (3) of Section 3.15. These WGRs must conduct engineering studies using the Summer/Fall 2010 Voltage Profiles to determine their actual Reactive Power capability and must, at a minimum, provide Reactive Power proportional to the real power output (a Reactive Power profile depicted graphically as a triangle). This NPRR further requires that all new Generation Resources shall have an engineering study, or demonstrate through performance testing, to show compliance with the Reactive Power capability requirements of paragraph (3) of Section 3.15 before beginning commercial operations. This NPRR also modifies the definition of “Automatic Voltage Regulator (AVR)” to better address the practical differences in Resource technology in providing this capability. |  |  |
| Reason for Revision |  | This NPRR addresses the central issue (a Reactive Power profile as either a rectangle or triangle) in PUC Docket No. 37817, Appeal and Complaint By Iberdrola Renewables, Inc. et al of ERCOT Decision to Approve PRR 830, and PUC Docket No. 38981, Joint Appellants’ Appeal and Complaint Concerning the ERCOT Board’s Adoption of NPRR 269 and Request for Related Relief. Order No. 22 (PUC Docket No. 37817) and Order No. 7 (PUC Docket No. 38981) consolidated PUC Docket No. 38981 into PUC Docket No. 37817. ERCOT and Joint Appellants have been working for some time to resolve the central issue involved in this PUC Docket. This NPRR is the work product of those efforts. All parties in PUC Docket No. 37817 have reviewed this NPRR. |  |  |
| Overall Market Benefit |  | Provides clarity on Reactive Power capability requirements to Existing Non-Exempt WGRs and better ensures that future Generation Resources are capable of meeting the Reactive Power capability requirements at time of commercial operations. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR389 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 7/6/11, NPRR389 and a preliminary Impact Analysis were posted. - On 7/20/11, Appellants in PUC Docket No. 37817 comments were posted. - On 7/21/11, PRS considered NPRR389. - On 8/11/11, an Impact Analysis was posted. - On 8/18/11, PRS considered the 7/21/11 PRS Report and Impact Analysis for NPRR389. |  |  |
| PRS Decision |  | On 7/21/11, PRS voted to recommend approval of NPRR389 as submitted. There was one abstention from the Investor Owned Utility (IOU) Market Segment. All Market Segments were present for the vote. On 8/18/11, PRS unanimously voted to endorse and forward the 7/21/11 PRS Report and Impact Analysis for NPRR389 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 7/21/11, ERCOT Staff explained that NPRR389 is intended to facilitate settlement of PUC Docket No. 37817. It was noted that interested parties in the wind generation community support NPRR389. On 8/18/11, there was no discussion. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provides clarity on Reactive Power capability requirements to Existing Non-Exempt WGRs and better ensures that future Generation Resources are capable of meeting the Reactive Power capability requirements at time of commercial operations. | To be determined. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Bill Magness / Chad V. Seely |
| E-mail Address | bmagness@ercot.com / cseely@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 225-7076 / (512) 225-7035 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jonathan Levine |
| E-Mail Address | jlevine@ercot.com |
| Phone Number | (512) 248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Appellants in PUC Docket No 37817 072011 | Endorsed NPRR389 as submitted and stated that approval of NPRR389, followed by ERCOT approval of appellants’ implementation plans and Public Utility Commission of Texas (PUCT) approval of the settlement agreement and issuance of a final order, will fully resolve Docket No. 37817. |

Comments

Please note that NPRR366, Generation Resource Power Factor Criteria Clarification, also proposes revisions to Section 3.15.

Proposed Protocol Language Revision

2.1	DEFINITIONS

Automatic Voltage Regulator (AVR)

A device on a Generation Resource or a control system at the Facility of a Generation Resource used to automatically control the voltage to an established voltage set point.

3.15	Voltage Support

(1)	ERCOT in coordination with the Transmission Service Providers (TSPs) shall establish and update, as necessary, the ERCOT System Voltage Profile for all Electrical Buses used for Voltage Support in the ERCOT System and shall post all Voltage Profiles on the Market Information System (MIS) Secure Area.  ERCOT may temporarily modify its requirements based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT. Generation Resources shall comply with the following Reactive Power Requirements:  an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.  The Reactive Power requirements shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Wind-powered Generation Resources (WGRs), the Reactive Power requirements shall be available at all MW output levels at or above ten percent of the WGR’s nameplate capacity.  When a WGR is operating below ten percent of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require a WGR to disconnect from the ERCOT System for purposes of maintaining reliability.  As part of the technical Resource requirements to begin commercial operations, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this paragraph.  Any study or testing results must be accepted by ERCOT prior to commercial operations.  The Reactive Power requirements of this paragraph shall apply to all Generation Resources except as otherwise provided in paragraphs (4) through (6) below.

(4)	WGRs that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in subparagraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles to determine their actual Reactive Power capability.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: (i) the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study; or (ii) Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results to ERCOT no later than five (5) Business Days after its completion;

(ii)	Existing Non-Exempt WGRs shall update any and all Resource registration information regarding their Reactive Power capability documented by the engineering study results;

(iii) 	If the Existing Non-Exempt WGR’s engineering study results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five (5) Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource registration information regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, to confirm accuracy of Resource registration information supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) and (4) above, multiple generation units including wind turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	WGRs must provide a Real Time Supervisory Control and Data Acquisition (SCADA) point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

WGRs must comply with the requirements of paragraph (12) by no later than June 1, 2010.

(13)	For the purpose of complying with the Reactive Power requirements under this Section, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.