## Slide 1: NPRR 365 Change in Resource Outage Approvals from 8 to 45 or 90 Days
Woody Rickerson
Director Grid Coordination
8-29-11

## Slide 2: Currently 2 Proposals
Original ERCOT NPRR365 language
PRS recommendation from 8/18/11
While both proposals would result in an improvement in ERCOT’s current ability to proactively coordinate outages, ERCOT continues to support the language in the original NPRR as filed by ERCOT.

## Slide 3
RT+7
TD+4
Real –Time
(RT)
Current Outage Scheduling Rules
Approval
Window
Approval
Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+37
Approval
Window
RT+82
RT+75
RT+30
Requires Approval
Automatically Accepted
RT+70
CRR
Deadline
RT+7
TD+4
Real –Time
(RT)
NPRR365 - ERCOT Submitted Version
Approval
Window
Approval
Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+37
Approval
Window
RT+82
RT+75
RT+30
Requires Approval
Automatically Accepted
RT+70
CRR
Deadline
Change
(Resource Outages)
(Resource Outages)
8-day

## Slide 4
NPRR365 - ERCOT Submitted Version
NPRR365 - PRS Version
Real –Time
(RT)
RT+70
NEW Extended
Approval Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+42
RT+82
RT+75
Automatically Accepted
CRR
Deadline
Automatically Accepted
Requires Approval
NEW Conflict Notification
Existing
Approval
Window
Existing
Approval
Window
Existing
Approval
Window
Change
RT+7
TD+4
Real –Time
(RT)
Approval
Window
Approval
Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+37
Approval
Window
RT+82
RT+75
RT+30
Requires Approval
RT+70
CRR
Deadline
(Resource Outages)
(Resource Outages)

## Slide 5
NPRR365 - PRS Version
Real –Time
(RT)
RT+70
NEW Extended
Approval Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+42
RT+82
RT+75
Automatically Accepted
CRR
Deadline
Requires Approval
NEW Conflict Notification
Existing
Approval
Window
Existing
Approval
Window
Existing
Approval
Window
Change
(Resource Outages)
Description of the PRS changes
1. Conflict Notification – If two conflicting Resource outages are submitted with more than 45-days notice, ERCOT will notify submitters within 5 business days if a conflict exists. Same risk exists today.
Remedy – notification will occur using the already established Approval Windows
2. New Extended Approval Window – Outages submitted with less than 45-days notice will be responded to within 3 business days. Increases approval windows by 300%.
Remedy - notification will occur using the already established Approval Windows
3. Moving the Acceptance/Approval deadline to 45 days instead of 90 days – No direct cost associated with move. Move will result in continued re-coordination of Transmission Outages and a potentially less accurate CRR model.
No Remedy, continued inefficiency

## Slide 6: Overall Cost of ROS/PRS Changes
ERCOT Version of NPRR365
  2 months to implement
  No staffing impact
  $15K - $20K
ROS/PRS Version of NPRR365
  5 to 8 months to implement
  Requires 4 new FTEs
  $125K - $150K
Real –Time
(RT)
RT+70
NEW Extended
Approval Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+42
RT+82
RT+75
Automatically Accepted
CRR
Deadline
Requires Approval
NEW Conflict Notification
Existing
Approval
Window
Existing
Approval
Window
Existing
Approval
Window
Change
(Resource Outages)

## Slide 7: Why 90 instead of 45
Most Planned Resource Outages should be submitted with more than 90-days notice no matter where the Acceptance/Approval rule is set.
At least 90-days is needed to coordinate potential EPA mandated CSAPR outages
CREZ outage construction requires long lead times, especially when the stability limits of the West are considered
Seasonal Outage Planning is only possible with a 90-day timeline.
A 90-day timeline provides more surety to the CRR model

## Slide 8: 1. Most Planned Resource Outages should be Automatically Accepted
If 90-day rule is implemented, Planned Resource Outages would still be automatically accepted as submitted if received with more than 90-days notice. This is already a requirement in existing Protocol language.
ERCOT Nodal Protocols
3.1.3.2 Resources
Each Resource Entity shall provide to ERCOT a Planned Outage and Maintenance Outage plan for Generation Resources in an ERCOT-provided format for the next 12 months updated monthly. Planned Outage and Maintenance Outage scheduling data must be kept current. Updates, through an electronic interface as specified by ERCOT, must identify any changes to previously proposed Planned Outages or Maintenance Outages and any additional Planned Outages or Maintenance Outages anticipated over the next 12 months.
Resource Outages submitted with less than 90-days notice will still be approved, but will be subject to ERCOT coordination if necessary.
ERCOT’s refusal rate for Planned Resource Outages (currently those submitted with 8 days or less notice) is extremely low. None have been rejected this year out of 380 possible submissions.

## Slide 9: 2. EPA CSAPR-triggered Resource Outages automatically accepted with as little as 46-days notice are not manageable.
3000 - 6000 MW of generation potentially affected
Outages needed for CSAPR work will likely require extended periods of time
CSAPR-related outages could potentially extend into 2013.
Already Tight Reserve Margins will require critical coordination with other Resource and Transmission Outages.

## Slide 10: 3. CREZ triggered construction Outages will peak in the fall of 2012.
Outages in the West already require more coordination because they often have to be accompanied with stability studies.
CREZ related outages must be coordinated with Resource Outages in order for CREZ construction to be completed on time.
45-days Notice is not adequate. ERCOT is already meeting with TSPs to coordinate Spring of 2012 Outages.

## Slide 11
STEC
11/1
Nov 2010
Dec 2010
Jan 2010
Feb 2011
Mar 2011
April 2011
Alberta Rd – Pharr Rebuild
AEP
11/23
Ajo
Res
12/16
Res
Res
Res
Res
Res
1/19
1/17 – 3/25
1/25 – 1/28
12/28 – 1/28
1/7 – 1/28
AEP
1/27
Ajo
2/8 – 2/11
ext
ext
ext
2/11
Extreme
Cold
2/3
AEP
3/26
A
Maintenance Level
3/27 – 3/27
4. Seasonal Outage Planning will help avoid re-coordination problems
78
62
14

## Slide 12
5. 90-days will provide more surety to the CRR model used in CRR Auctions
RT+7
TD+4
Real –Time
(RT)
Approval
Window
Approval
Window
90-day
Timeline
45-day
Timeline
9-day, 4-day, 3-day
Timelines
RT+1
RT+37
Approval
Window
RT+82
RT+75
RT+30
RT+70
CRR Snapshot
Deadline
Resource Outages submitted with 45-90 days notice will have the potential to displace transmission outages that were included in the CRR snapshot if the Acceptance/Approval timeline is placed at 45-days.
?

## Slide 13: No other ISO automatically accepts any Planned Resource Outages
New England ISO – Planned outages are submitted before February 15th each year for the Commitment Period which starts in June. Planned Outages are subject to NEISO approval and rescheduling. Maintenance outages can be submitted up to 1 day ahead and are subject to NEISO coordination.
Californian ISO – Resource planned maintenance outages are submitted by October 15th, for the following calendar year. The submittals look forward 15 months. The plans are updated on a quarterly basis. CAISO approve or reject all requests within 30 days of receipt. Maintenance outages are evaluated on a daily basis and are subject to CAISO coordination.
Midwest ISO – Resources submit Planned outages 24 months in advance and update the schedule on a daily basis. All requests are subject MISO approval. Maintenance outages are evaluated on a daily basis and are subject to MISO approval.
PJM – Resources submit Planned Outages at least 30-days in advance of the outage. PJM can approve or reject the requests. Maintenance outages (limited to 9 days during peak times) can be submitted at any time and are subject to PJM postponement or rejection.
NYISO – Resources provide a 3-year schedule of Planned outages by July 1st each year (6 months prior to that start of the 3-yr period). The Planned outages are subject to NYISO review and rescheduling. Maintenance outages must be submitted 30-days in advance and are subject to NYISO approval and coordination.
ERCOT – Planned Resource Outages are submitted on a rolling 12-month plan. ERCOT accepts all Outages submitted with more than 8 days notice and approves or rejects Outages with less than 8 days or less notice.

## Slide 14: NERC/FERC Report on “Outages and Curtailments During the Southwest Cold Weather Event of February 1-5, 2011.
  Page 53 “ERCOT is a summer peaking system, and the high summer temperatures and demand often extend into what would be considered shoulder seasons in more northerly regions. For that reason, it is not unusual for generators in ERCOT to schedule maintenance outages in February. ERCOT does not have the authority to prohibit generators from scheduling such outages or from taking them as scheduled, unless the outage is scheduled eight days or less before the outage date, or the outage would keep ERCOT from meeting applicable Reliability Standards or its own Protocol requirements. At most, pursuant to its Protocols, ERCOT can ask generators to refrain from taking a scheduled outage if it believes it may need the generator’s output. ERCOT also does not have authority under its Protocols to require generators that are on planned outage to come back into service early (assuming the generator is even in a condition to do so).
  Page 198 “ERCOT should reconsider its protocol that requires it to approve outages if requested more than eight days before the outage, consider giving itself the authority to cancel outages previously scheduled, and expand its outage evaluation criteria.
  Page 199. “The task force recommends that ERCOT consider lengthening the period for which ERCOT may deny an outage request, assuming the conditions for doing so are met. (ERCOT is presently considering a Protocol revision to give itself the authority to deny an outage request that is not scheduled more than 90 days prior to the outage date, a revision which the task force supports.) In addition, ERCOT should consider giving itself the authority to cancel previously approved outages in cases of approaching extreme weather conditions, even up to the time of the event itself.