## Slide 1: Lower Rio Grande Valley Regional Planning Group Project
Jeff Billo
Manager, Mid-Term Planning

## Slide 2: LRGV Import Background
The Lower Rio Grande Valley (LRGV) is currently served by:
  (2) 345 kV lines,
  (3) 138 kV lines,
  approximately 1700 MW natural gas generation, and
  150 MW DC tie to Mexico
On February 3, 2011 the LRGV experienced load levels greatly exceeding the previous planning forecast for 2011, highlighting the need for additional transmission infrastructure to serve the area

## Slide 3
RPG Review
AEPSC proposed initial project in March, following February event (project had been in planning discussions well before)
ERCOT and AEPSC studies showed ERCOT planning criteria would be exceeded in 2016 without system upgrades
RPG Comment Period was held during April (and a second comment period was held on the final options in August)
  RPG participants submitted alternative transmission solutions and ERCOT identified additional alternatives
  Several commenters discussed the potential for generation solutions; ERCOT does not have the authority to implement generation additions but does have planning criteria obligations
AEPSC modified its proposal to enable the project to meet 2016 requirements
Status reports on the ERCOT Independent Review were discussed at each monthly RPG meeting

## Slide 4: Independent Review Study Approach
Evaluated 2016 summer peak SSWG case and 2020 summer peak case from the ERCOT/ DOE long-term study
  Modified cases to use latest load forecasts from AEPSC
  Removed 250 MW load addition in Brownsville (Brownsville needs are being analyzed in separate RPG review)
  Set nearby wind output at 10% of capacity (based on 2010 historical data, 10th percentile output of coastal wind plants)
Performed AC contingency analysis and steady-state voltage stability analysis
  With largest unit (combined cycle in LRGV) out of service per ERCOT planning criteria
Focused analysis on 2016 reliability; also evaluated 2020 reliability and N-1-1 (maintenance outage) scenarios
Nine distinct alternatives were evaluated and narrowed to three final alternatives

## Slide 5: Three Project Alternatives for Final Consideration
Option 1R: $525 million
Lobo-Rio Bravo-N. Edinburg 163 mile single circuit 345 kV line with 50% series compensation
Energized reconductor of Lon Hill-N. Edinburg and Lon Hill-Rio Hondo 345 kV lines
Reconfigure N. Edinburg and Rio Hondo series capacitors
Reconductor
Option 5D: $508 million
Pawnee-N. Edinburg 200 mile double circuit 345 kV line with 50% series compensation on each circuit
Option 6: $659 million
Pawnee-Loma Alta 220 mile 1000 MW classic HVDC
Loma Alta 345 kV bus with (2) 345/138 kV autotransformers
Loma Alta-La Palma 14 mile 345 kV line

## Slide 6: 2016 LRGV Load Serving Capability Results (G-1 + N-1)
MW

## Slide 7: 2016 LRGV N-1-1 Load Serving Capability Results
MW

## Slide 8: 2020 LRGV Load Serving Capability Results (G-1 + N-1)
MW

## Slide 9: ERCOT Independent Review Results
 | Option 1R | Option 5D | Option 6
Project cost in 2016 | $ 525 million | $ 508 million | $ 659 million
2016 load serving capability (MW) | 2949 | 3205 | 3265
2016 N-1-1 (Maintenance outages) load serving capability | 2826 | 3065 | 3065
Additional system upgrades needed in 2016 | Raymondville-Harlingen Switch 69 kV (18.1 miles) | Lon Hill-Smith-Edroy 69 kV (11.6 miles) and Raymondville-Harlingen Switch 69 kV (18.1 miles) | Lon Hill-Smith-Edroy-Mathis 69 kV (25.4 miles) and Loma Alta-South Carbide 138 kV (1.1 miles)
2020 load serving capability (MW) | 3095 | 3160 | 3298
Potential Project cost in 2020 (including infrastructure improvements for Laredo and Brownsville) | $627 million | $600 million | $709 million
Geographical diversity of the new line | Excellent | Good | Good
Total new ROW required (2016/2020) | ~163/~202 miles | ~200/~244 miles | ~234/~264 miles
Rehabilitation of existing Lon Hill-Rio Hondo and Lon Hill-North Edinburg 345 kV lines | Yes | No | No
Infrastructure Improvement in the area of new generation interconnection projects | Good | None | Fair
Projected in-service date (estimation provider) | 2016 (AEPSC) | 2017 (AEPSC) | 2016 (Sharyland)

## Slide 10: Conclusions
ERCOT will request the ERCOT BOD endorse the following improvements associated with Option 1R:
  Construct a new 163 mile, single circuit 345 kV line from Lobo to Rio Bravo to North Edinburg, utilizing 2-954 ACSR conductor on double-circuit capable structures, and (2) approximately 24 ohm 3600 amp series capacitors on the Lobo 345 kV circuit (no additional substation equipment would be installed at Rio Bravo at this time but may be added in the future as needed to support the Laredo area needs)
  Reconductor the existing Lon Hill-Nelson Sharpe-Ajo-Rio Hondo 345 kV line to 1988/2426 MVA normal/emergency rating to achieve increased rating before peak of 2016
  Reconductor the existing Lon Hill-North Edinburg 345 kV line to 1988/2426 MVA normal/emergency rating to achieve increased rating before peak of 2016
  Reconfiguration of the North Edinburg and Rio Hondo series capacitors such that the MVA rating is at least 2000 MVA and the compensation level is 25% of each respective circuit
Estimated Capital Cost = $525M
ERCOT will also ask that the BOD deem the project critical to reliability in accordance with PUCT Substantive Rule 25.101 (b)(3)(D)

## Slide 11
Questions?