| NOGRR Number | 067 | NOGRR Title | Review and Analysis of Turbine Speed Governor Performance |
| --- | --- | --- | --- |

| Date | June 20, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Randy Jones |
| E-mail Address | rajones@calpine.com |
| Company | Calpine |
| Phone Number | 713.830.8846 |
| Cell Number | 832.385.3322 |
| Market Segment | Independent Generator |

Comments

Calpine submits these edits and comments in an effort to incorporate some of the issues discussed by the PDCWG in its recent efforts to examine Responsive Reserve (RRS) Service in a holistic way.

The ERCOT wholesale market design has changed considerably over the last ten years and both the Protocols and Operating Guides have not kept up as well as they should have with changes in technology and market dynamics brought on by changing market design.  Rules for speed governor operation have lagged behind noticeably and continue to reflect more the operation of older vintage steam turbine operation in a bundled rate, vertically integrated system where key reliability services such as governor response and voltage support were not explicitly priced out. Our market rules are only beginning to catch up on the control performance of combined-cycle resources and wind generators in regard to turbine governor performance.  For example, the Operating Guide requirements for the speed droop testing of combustion turbines was only approved a few years ago, while combined-cycle combustion turbines have been a part of the ERCOT system since 1985.

The market’s economics have been optimized to the point that at times many of the units online are loaded up to their High Sustained Limit (HSL) and not able to fully respond with a 5% droop characteristic due to being in exhaust temperature control in order to supply the market’s energy needs while protecting the machine’s internal parts. This condition is just one of many that call for adding more details to the rules surrounding Primary Frequency Response because the literal interpretation of the existing rules does not recognize the realities in today’s system. Those units not providing RRS or other Ancillary Services should not always be expected to provide Primary Frequency Response (currently a free, yet mandatory service) for low frequency events. Calpine encourages other technologies to contribute edits that will better reflect their machines’ different characteristics.

Revised Proposed Guide Language

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.

(2)	Resource Entities shall conduct Governor performance tests for each Generation Resource or Wind-powered Generation Resource (WGR) at least every two years using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	Every effort should be made to maintain Primary Frequency Response consistent with the Generation Resource’s loading at the time of an event. Performance Tests on Governors shall demonstrate calibration for operation consistent with a generator droop characteristic of no greater than 5% but no less than 2% and Governor Dead-Band no greater than +/- 0.036 Hz.

(4)	There are elements that can contribute to poor Primary Frequency Response.  These include:

(a)	Governor Dead-Band in excess of +/- 0.036 Hz (measured from 60 Hz);

(b)	Valve position limits;

(c)	Blocked Governor operation;

(d)	Control mode (note: combustion turbine in turbine exhaust temperature control mode is an acceptable mode of operation);

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(5)	 Attempts should be made to minimize the effects of the elements listed in item (4) above on the Governor operation.  Each Resource Entity should monitor its Generation Resources to verify these elements do not contribute to a Governor droop characteristic  greater than 5% or less than 2%.

(a)	Acceptable Governor operation of Generation Resources not providing RRS shall be governor action in the correct direction for the frequency deviation, coupled with a measurable MW contribution at the B Point measurement point as well as at the B+30 Point second measurement point.  An exception shall be granted for combined-cycle units whose synchronous compressors’ reduced speed in response to frequency declines resulting in negative governor response.

(6)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct WGRs under the control of a Special Protection System (SPS) to limit power increases due to frequency if there is risk of an SPS operation due to a low frequency event.