| NOGRR Number | 067 | NOGRR Title | Review and Analysis of Turbine Speed Governor Performance |
| --- | --- | --- | --- |

| Date | August 10, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Sydney Niemeyer on behalf of the Performance Disturbance Compliance Working Group (PDCWG) |
| E-mail Address | Sydney.niemeyer@nrgenergy.com |
| Company | NRG Energy |
| Phone Number | 713-537-3715 |
| Cell Number | 832-655-0410 |
| Market Segment | Generator |

Comments

The PDCWG is in consensus to endorse Nodal Operating Guide Revision Request (NOGRR) 067 as recommended by the Operations Working Group (OWG) on June 15, 2011 as it concerns clarification of the responsible Entity for monitoring Generation Resources during frequency events.  However, in response to the discussion at the 7/20/11 OWG meeting regarding PDCWG’s holistic review of Primary Frequency Response, the PDCWG agreed to clarify requirements for Primary Frequency Response of Resources that provide Ancillary Services in the ERCOT Region in a future NOGRR since Section 2.2.7, Turbine Speed Governors, does not address Ancillary Services.

Revised Proposed Guide Language

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.

(2)	Resource Entities shall conduct Governor performance tests for each Generation Resource or Wind-powered Generation Resource (WGR) at least every two years using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	Every effort should be made to maintain Primary Frequency Response. Maintenance  Tests on Governors shall demonstrate calibration for operation consistent with a generator droop characteristic of no greater than 5% but no less than 2% and Governor Dead-Band no greater than +/- 0.036 Hz.

(4)	There are elements that can contribute to poor Primary Frequency Response.  These include:

(a)	Governor Dead-Band in excess of +/- 0.036 Hz (measured from 60 Hz);

(b)	Valve position limits;

(c)	Blocked Governor operation;

(d)	Control mode;

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(5)	Every attempt should be made to minimize the effects of the elements listed in item (4) above on the Governor operation for the duration of all frequency deviations.  Each Resource Entity should monitor its Generation Resources to verify these elements do not contribute to a Governor droop characteristic of no greater than 5% but no less than 2%.

(6)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct WGRs under the control of a Special Protection System (SPS) to limit power increases due to frequency if there is risk of an SPS operation due to a low frequency event.