## Slide 1: PDCWG Report to ROS
September 15, 2011
Sydney Niemeyer

## Slide 2: In This Report
NERC Reliability Metrics Working Group metric on Interconnection Primary Frequency Response.
ERCOT Frequency Control Performance – August.
PDCWG On-going work.
  Wind Generator Primary Frequency Response implementation

## Slide 3: ERCOT Average Primary Frequency Response
NERC – Reliability Metrics Working Group Interconnection Performance Metric.
  Standard measurement for all North American Interconnections.
  Metric for frequency response performance from Nov, 2008 through present.

## Slide 5
ERCOT 2012 Bias Calculation Period
Primary Frequency Response Performance

## Slide 6: ERCOT Frequency Control Performance
August, 2011

## Slide 7
Steady and consistent performance everyday!

## Slide 10
Daily RMS1 data also indicates consistent performance.

## Slide 17: PDCWG On-going Work
Participating in the NERC BAL-003 Primary Frequency Response Field Trial.
  Frequency Response performance was submitted to NERC and is being reviewed by the standard drafting team. 45 frequency events through Aug 1, 2011 were evaluated resulting in an average performance of -533.8 MW/0.1 Hz with a frequency response obligation of -286 MW/0.1 Hz as the minimum performance level.
Review of Wind Generation Primary Frequency Response implementation to determine if planned implementations will meet the protocols, guides and performance measures.
  Concerns with dead-band settings.
  Concerns with step-response when frequency returns to values within the dead-band and production potential is significantly different.
Implementation of NPRR 258 will require Generator Owners to report Governor Droop and Dead-band settings to ERCOT for correct calculation of Expected Primary Frequency Response in GREDP and for event PFR evaluation.
PDCWG next meeting is October 4, 2011

## Slide 18
Questions?