## Slide 1: Elimination of Time Error Correction Potential Impact on Wholesale Settlements
Presentation RMS
Aug 17, 2011
RMS Meeting Discussion

## Slide 2: Background
Presentation RMS
Aug 17, 2011
NERC Operating Committee (OC) directed the Resources Subcommittee (RS) to develop a field trial to eliminate manual Time Error Corrections
What is Time Error?
  Difference between NIST time and a clock driven by frequency
    If average frequency is 60Hz, Time Error will be zero
    If frequency is 0.01Hz high (low), a clock will gain (lose) 0.6 seconds an hour
What are Manual Time Error Corrections ?
  Minor coordinated adjustments to frequency
  One Reliability Coordinator in each Interconnection is designated “Time Monitor”
  ERCOT Nodal Operating Guide Section 2.2.9.1 deals with time error
    When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction
    Correction may end when error is less than ±0.5 seconds or when system events mandate termination
    Time correction may be postponed if it is determined that load patterns in immediate future will result in desired time correction

## Slide 3: Impact of Elimination of Time Error Correction on Wholesale Settlements
Presentation RMS
Aug 17, 2011
Assume that ERCOT Polled Settlement (EPS) meters will be synchronized with NIST clock
Potential effect on wholesale settlements is analyzed for following:
  Flat load
  Price responsive load and/or demand responsive load
    Different MW load connected to the IDR meter-100 to 1150 MW
    Different delays (lag and lead)- 15 sec, 30 sec and 45 sec
    Different price levels- $200 to $3000 /MWH
  Aggregate IDR load in grid
Maximum allowed time error according to ERCOT Nodal Protocol 10: Metering
  For TDSP meters: ±5% of settlement interval (15 min) or 45 sec of NIST clock
  For EPS meters : ±1% of settlement interval (15 min) or 9 sec of NIST clock
  ERCOT production servers are maintained within ±1 sec of NIST clock
    Wholesale price calculations synchronized within ±1 sec of NIST clock for each settlement interval
No analysis conducted for retail settlements
  Results contingent on contracts and specific load characteristics

## Slide 4: Price/Demand Responsive Load IDR slower than NIST clock by 30 sec, 150 MW load
Presentation RMS
Aug 17, 2011
-Delayed IDR Clock
-NIST Clock
Interval 1
Interval 2
Interval 3
Interval 4
Interval 5
30 sec delay
16:45:00
16:30:00
150 MW
150 MW
$35/ MWH
$35/ MWH
0 MW
37.5 MWH
36.25 MWH
0 MWH
1.25 MWH
37.5 MWH
16:15:00
16:00:00
$1000/ MWH

## Slide 5: Price/Demand Responsive Load Excel Worksheet for Calculation
Presentation RMS
Aug 17, 2011
Fill in the following values: 1. Load (MWH)
2. Time deviation (sec)
3. Price ($/MWH )in each interval

## Slide 6: Price/Demand Responsive Load IDR slower than NIST clock by 30 sec, 150 MW load
Presentation RMS
Aug 17, 2011
 | MWH in Interval |  | Price in Interval ($/MWH) | Total Price in Interval ($) | 
 | Expected MWH (w/o clock lag) | Actual MWH (with clock lag) |  | Expected Price (w/o clock lag) | Actual Price (with clock lag)
Interval 1 | 37.5 | 37.5 | $35 | $1,312.5 | $1,312.5
Interval 2 | 37.5 | 36.25 | $35 | $1,312.5 | $1,268.75
Interval 3 | 0 | 0 | $1000 | $0 | $0
Interval 4 | 0 | 1.25 | $1000 | $0 | $1,250.00
Interval 5 | 37.5 | 37.5 | $35 | $1,312.5 | $1,312.5
Total Price |  |  |  | $3,937.50 | $5,143.75
Net Loss |  |  |  | $1,206.25 | 

## Slide 7: Price/Demand Responsive Load Effect of Time Delay at Different Load Levels
Presentation RMS
Aug 17, 2011
Price in Interval 4: $1000/MWH
Price in Interval 2: $35/MWH
Note:
Net losses calculated over entire 5 interval event

## Slide 8: Price/Demand Responsive Load Effect of Time Delay at Different Price Levels
Presentation RMS
Aug 17, 2011
Price in Interval 4: $200/MWH
Price in Interval 4: $500/MWH
Price in Interval 4: $1000/MWH
Price in Interval 4: $3000/MWH
Note: Net losses calculated over entire 5 interval event

## Slide 9: Price/Demand Responsive Load IDR faster than NIST clock by 30 sec, 150 MW load
Presentation RMS
Aug 17, 2011
-Accelerated IDR Clock
-NIST Clock
Interval 1
Interval 2
Interval 3
Interval 4
Interval 5
30 sec delay
16:45:00
16:30:00
150 MW
150 MW
$35/ MWH
$35/ MWH
0 MW
37.5 MWH
36.25 MWH
0 MWH
1.25 MWH
37.5 MWH
16:15:00
16:00:00
$1000/ MWH
Losses and savings intervals interchanged
Values remain same

## Slide 10: Aggregate IDR Load IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
-Delayed IDR Clock
-NIST Clock
Interval 1
Interval 2
Interval 3
30 sec delay
10,000 MWH
10,200 MWH
10,400 MWH
Energy Recorded by IDR In Interval 2 = Energy Consumed in Interval 2 + Metered Energy Shifted from Interval 3 to 2 -
Metered Energy Shifted from Interval 2 to 1
Note: IDR accounts for 70% of total grid load
10,206.67 MWH = 10,200.00 MWH + 346.67 MWH – 340.00 MWH

## Slide 11: Aggregate IDR Load IDR faster than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
- Accelerated IDR Clock
-NIST Clock
Interval 1
Interval 2
Interval 3
30 sec delay
10,000 MWH
10,200 MWH
10,400 MWH
Energy Recorded by IDR In Interval 2 = Energy Consumed in Interval 2 + Metered Energy Shifted from Interval 1 to 2 -
Metered Energy Shifted from Interval 2 to 3
Note: IDR accounts for 70% of total grid load
10,193.33 MWH = 10,200.00 MWH + 333.33 MWH – 340.00 MWH

## Slide 12: Aggregate IDR Load Example: June 09, 2011 IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
Average Shift in Interval Load Due to IDR Delay: 0.0006%
Average UFE: 0.4000%

## Slide 13: Aggregate IDR Load Example: April 21, 2011 IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
Average Shift in Interval Load Due to IDR Delay: 0.0014%
Average UFE: 0.3606%

## Slide 14: Aggregate IDR Load Example: Dec 21, 2010 IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
Average Shift in Interval Load Due to IDR Delay: 0.0004%
Average UFE: -1.2298%

## Slide 15: Aggregate IDR Load Example: Jul 8, 2011 IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
Average Shift in Interval Load Due to IDR Delay: 0.0014%
Average UFE: 1.0757%

## Slide 16: Aggregate IDR Load Example: Feb 2, 2011 IDR slower than NIST clock by 30 sec
Presentation RMS
Aug 17, 2011
Average Shift in Interval Load Due to IDR Delay: 0.0007%
Average UFE: 1.9799%

## Slide 17: Summary
Presentation RMS
Aug 17, 2011
Observations of this study are as follows:
  Flat load
    No Impact
  Price/demand responsive load
    Potential impact. Will depend on site operating procedures and load characteristics
    IDR clock error combined with variations in price of electricity will result in savings in one interval, with losses in other
  Aggregate IDR load
    Meter clock error up to 45 seconds has minimal impact on aggregate IDR load used in wholesale settlements
    IDR clock error combined with variations in price of electricity will result in savings in one interval, with losses in other
Note: Study of impact of elimination of time error correction on retail settlements or an individual market participant has not been performed. Each individual party should carry out their own study based on their specific load characteristics

## Slide 18
Presentation RMS
Aug 17, 2011
Questions?