| NOGRR Number | 067 | NOGRR Title | Review and Analysis of Turbine Speed Governor Performance |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | June 15, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Section Requiring Revision |  | 2.2.7, Turbine Speed Governors |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) clarifies the Entity responsible for monitoring Generation Resources during frequency events. |  |  |
| Reason for Revision |  | The current language does not accurately reflect the Entity responsible for monitoring Generation Resources frequency events. |  |  |
| Overall Market Benefit |  | Clarifies Entity responsible for monitoring Generation Resource during frequency events. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 3/10/11, NOGRR067 was posted. - On 3/21/11, Luminant Energy comments were posted. - On 3/21/11, LCRA comments were posted. - On 4/13/11, Performance, Disturbance, Compliance Working Group (PDCWG) comments were posted. - On 4/20/11, the Operations Working Group (OWG) considered NOGRR067. - On 5/18/11, the OWG again considered NOGRR067. - On 6/13/11, a second set of Luminant comments were posted. - On 6/15/11, OWG again considered NOGRR067. |  |  |
| OWG Decision |  | On 4/20/11, the OWG was in consensus to table NOGRR067 for one month. On 5/18/11, the OWG was in consensus to table NOGRR067. On 6/15/11, the OWG was in consensus to recommend approval of NOGRR067 as amended by the 6/13/11 Luminant comments. |  |  |
| Summary of OWG Discussion |  | On 4/20/11, the 4/13/11 PDCWG comments were discussed. It was requested that the OWG table NOGRR067 to allow time for interested parties to discuss the concerns raised by the PDCWG. It was also noted that additional review of NOGRR067 is needed as there could be a need to incorporate changes related to North American Electric Reliability Corporation (NERC) Reliability Standard BAL-001, Real Power Balancing Control Performance. On 5/18/11, it was noted that additional review of NOGRR067 is needed as there could be a need to incorporate changes related to NERC Reliability Standard BAL-001. On 6/15/11, the 6/13/11 Luminant comments were discussed. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None | None |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  |  |  |
|  | 1 | Clarifies Entity responsible for monitoring Generation Resource during frequency events. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Henry Durrwachter |
| E-mail Address | hdurrwachter@luminant.com |
| Company | Luminant Energy Company LLC |
| Phone Number | 214-875-9285 |
| Cell Number | 214-437-4622 |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Luminant Energy 032111 | Proposed language changes that would require Resource Entities and not Qualified Scheduling Entities (QSEs) to submit turbine Governor speed tests and to review and analyze Generation Resource performance during frequency events. |
| LCRA 032111 | Proposed language changes to better align with the PDCWG’s scope of responsibilities. |
| PDCWG 041311 | Recommended rejection of NOGRR067. |
| Luminant 061311 | Proposed language changes to retain the change from the QSE to the Resource Entity as the responsible party for monitoring Generation Resources during frequency events and to restore some original Operating Guide language. |

Proposed Guide Language Revision

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.

(2)	Resource Entities shall conduct Governor performance tests for each Generation Resource or Wind-powered Generation Resource (WGR) at least every two years using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	Every effort should be made to maintain Primary Frequency Response. Maintenance  Tests on Governors shall demonstrate calibration for operation consistent with a generator droop characteristic of no greater than 5% but no less than 2% and Governor Dead-Band no greater than +/- 0.036 Hz.

(4)	There are elements that can contribute to poor Primary Frequency Response.  These include:

(a)	Governor Dead-Band in excess of +/- 0.036 Hz (measured from 60 Hz);

(b)	Valve position limits;

(c)	Blocked Governor operation;

(d)	Control mode;

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(5)	Every attempt should be made to minimize the effects of the elements listed in item (4) above on the Governor operation for the duration of all frequency deviations.  Each Resource Entity should monitor its Generation Resources to verify these elements do not contribute to a Governor droop characteristic of no greater than 5% but no less than 2%.

(6)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct WGRs under the control of a Special Protection System (SPS) to limit power increases due to frequency if there is risk of an SPS operation due to a low frequency event.