## Slide 1: PDCWG
Responsive Reserve Service Deliverability Review
September 15, 2011

## Slide 2: Introduction
Responsive Reserve Service Capacity as it relates to congestion and its deliverability.
Responsive Reserve Capacity during the February 2nd EEA event.
The potential affect of Responsive Reserve Service capacity that is not frequency responsive.
Responsive Reserve Service allocation limits on a single Resource, is the 20% capacity limit correct?

## Slide 3: Congested Responsive Reserve Service Capacity
SCED will utilize congested RRS capacity last.
Congested RRS capacity will continue to provide Primary Frequency Response even while congested.
  Governor In-service and free to respond to all frequency deviations outside Governor Dead-Band.
During EEA-2A and 2B, RRS Capacity on Generators will be utilized to maintain frequency at 60 Hz.
During EEA- 3, RRS Capacity on Generators will be utilized to maintain frequency above 59.80 Hz.

## Slide 4: Percent Time RRS Capacity Constrained
 |  |  |  | Percent of 5 minute intervals in a month when transmission constraint was affecting # of resources carrying RRS |  |  |  | 
Month-Year | AVG Number of Resources carrying RRS | Max Number of Resources carrying RRS | Min Number of Resources carrying RRS | 1-10 Resources | 10-20 Resources | 20-30 Resources | Greater than 30 Resources | sum
Dec-10 | 31 | 44 (1.20% intervals >35) | 13 (0.067%<20) | 12.34% | 5.42% | 10.21% | 7.59% | 35.56%
Jan-11 | 29 | 39(1.63% intervals >35) | 15 (0.201%<20) | 17.70% | 3.90% | 10.79% | 2.48% | 34.87%
Feb-11 | 44 | 85 (1.88% intervals >80) | 23 (0.174%<25) | 18.97% | 2.88% | 9.54% | 14.99% | 46.37%
Mar-11 | 37 | 48 (24.30% intervals > 40) | 23 (5.63% < 30) | 8.20% | 1.11% | 1.38% | 11.04% | 21.73%
Apr-11 | 37 | 54 (4.98% intervals > 45) | 23 (3.34% < 30) | 33.90% | 6.31% | 7.68% | 7.22% | 55.11%
May-11 | 34 | 47 (3.93% intervals > 40) | 19 (0.0112% < 25) | 26.72% | 10.62% | 13.80% | 9.01% | 60.15%
Slide provided by ERCOT, Constrained = Resource LMP more than $0.50 below system lambda.

## Slide 5: Data source and methods
5 minute sampled data
Telemetered Responsibility used to determine number of Resources carrying RRS
1% duration generally converts to roughly ninety 5-minute intervals (31 days month)
The number of resources carrying RRS may include up to 13 resources in Synchronous Condenser (Hydro)

## Slide 6: Responsive Reserve Service Capacity
During the February 2nd EEA event.

## Slide 7: Spinning Physical Reserve Feb 2, 2011
Frequency 59.80 Hz
Physical Reserve = 850 MW
Physical Reserve = 450 MW

## Slide 8: During Short Supply Periods
Responsive Reserve Service capacity can decrease to very low levels during EEA 2 and 3 events.
August 4 EEA 2B event, RRS capacity decreased to levels just below 1000 MW.

## Slide 9: The Potential Affect of Responsive Reserve Service Capacity
That is not frequency responsive.

## Slide 10: RRS Capacity that is not Frequency Responsive
If allowed, increases risk of UFLS significantly.
If constrained, non-frequency responsive capacity may never be utilized.
  With grid Primary Frequency Response depending totally on Load Dampening, frequency would be extremely sensitive to any imbalance. (If all RRS was not frequency responsive).
  Frequency could reach 59.300 Hz before capacity could be utilized by SCED and waiting on delivery. (Ten minute product vs. frequency responsive product).

## Slide 11
Recent Operation During EEA Step 2A and 2B Emphasizes An Important Difference
Regulation Up Service was fully deployed.
Load Resources were fully deployed.
SCED Up Capacity was limited to the capacity of un-deployed Responsive Reserve Service from Generators.
MW loss size assumes a starting frequency of 60.000 Hz.

## Slide 12: Summary
Responsive Reserve Service capacity that does not respond to changes in frequency, increases the risk that a relatively small Resource trip during short supply events will trip UFLS.

## Slide 13: Responsive Reserve Service Capacity Allocation Limits
Deliverability during sudden, extreme events (May 15, 2003).

## Slide 14: 20% Capacity Limit per Resource
The Governor of a Resource will deploy 20% of the capacity of a Resource if frequency deviates -0.600 Hz plus the Governor Dead-Band.
  At 59.364* Hz, the Governor will deploy 20% of the capacity of a Resource with a 5% Droop setting.
  Even if fully constrained by SCED, full RRS should be deployed by the Governor before the first stage of UFLS, 59.300 Hz, is reached.

## Slide 15: Resource Performance May 15, 2003
May 15, 2003 loss of 3434 MW and 59.29 Hz Point C and 59.46 Hz Point B. During the first minute of the event:
  16 Steam units responded with average 0.655 P.U. performance. (65.5 % of expected response)
  13 Combustion turbines responded with average 0.660 P.U. performance. (66% of expected response)
  Generators responding correctly provided 14% of their capacity on average in less than one minute.
    5 steam units provided 18% or greater.
    2 combustion turbines provided 18% or greater.
    5 combustion turbines provided 16% or greater.
    2 steam units provided 16% or greater.

## Slide 16: Summary
Is the 20% allocation limit correct for maximum deliverability during sudden, extreme events?