## Slide 1: Proposed 2012 Methodology for Determining Ancillary Service Requirements

## Slide 2: Regulation Service – Review of Current Methodology
Inputs for determining the monthly Regulation Service requirements include the following:
  Last 30 days of Regulation Service deployments
  5 minute net-load changes from the last 30 days and from the same month of the previous year
  Regulation Service requirement for the same month of the previous year divided by 2
    The division by 2 is intended to account for the fact that Regulation moved from a 10-minute product in Zonal to a 5-minute product in Nodal

## Slide 3: Regulation Service – Proposed Methodology Changes
A number of changes made during the last iteration of the document were done in preparation for the market transition
  Historical data from the Zonal Market would not necessarily be relevant or appropriate for the Nodal Market
The proposed changes are as follows:
  The Regulation Service deployments from the same month of the previous year will be considered along with the deployments from the last 30 days
  The Regulation Service requirement for the same month of the previous year divided by 2 will no longer be used as an input

## Slide 4: Non-Spin Reserve Service – Review of Current Methodology
For determining the monthly requirement:
  Break up the hours of the day into groups
  Calculate the 95th percentile of the day ahead net-load forecast error
  Set the requirement such that the combination of Non-Spin and Regulation Up Service will cover 95% of the net-load forecast error
  If it has been determined that the forecasts have shown a tendency to be conservative, that bias will be removed from the load forecast and added to the NSRS requirement
    This attempts to remove bias from forecasts while ensuring that reliability in maintained
  Both a floor and ceiling are placed on the requirement
    Floor during on-peak hours of single largest unit
    Ceiling of 2000 MW during all hours

## Slide 5: Non-Spin Reserve Service – Proposed Methodology Changes
Under the Nodal Market, Market Participants are more easily able to self commit Resources closer to Real-Time
  Because of this it may not be necessary to procure Non-Spin to protect against 1600 day ahead forecast error
Proposal is to use net-load forecast error from midnight instead of the 1600 day ahead error
  This should better align the ancillary service requirements with Nodal timelines
  The Regulation Up requirement will continue to be subtracted from the forecast error to determine the Non-Spin requirement

## Slide 6: Effects of Proposed Methodology on NSRS Requirement
The overall effect is that slightly less NSRS would be procured on average
  This varied by month
  The average effect on the value subtracted from the MTLF was insignificant
Month |  | Average Change in Non-Spin Requirement (*) | Average Change in Value Subtracted from the MTLF (**)
February 2011 |  | -6.67 | 0.00
March 2011 |  | 54.00 | -49.17
April 2011 |  | -231.50 | 55.33
May 2011 |  | 38.83 | 30.83
June 2011 |  | -190.33 | 147.67
July 2011 |  | -108.00 | -42.17
August 2011 |  | 105.50 | -126.00
* | A positive number means that more Non-Spin would be procured under the proposed methodology |  | 
** | A positive number means that a larger number would be subtracted from the MTLF under the proposed methodology |  | 

## Slide 7: Proposed Non-Spin Methodology Examples – March ‘11
Current Methodology
Proposed Methodology
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 2000 | -121
2 | 2000 | -121
3 | 2000 | 0
4 | 2000 | 0
5 | 2000 | 0
6 | 2000 | 0
7 | 2000 | 0
8 | 2000 | 0
9 | 2000 | 0
10 | 2000 | 0
11 | 2000 | 0
12 | 2000 | 0
13 | 2000 | 0
14 | 2000 | 0
15 | 2000 | -158
16 | 2000 | -158
17 | 2000 | -158
18 | 2000 | -158
19 | 2000 | 0
20 | 2000 | 0
21 | 2000 | 0
22 | 2000 | 0
23 | 2000 | -121
24 | 2000 | -121
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 2000 | 0
2 | 2000 | 0
3 | 2000 | -182
4 | 2000 | -182
5 | 2000 | -182
6 | 2000 | -182
7 | 1676 | -392
8 | 1676 | -392
9 | 1676 | -392
10 | 1676 | -392
11 | 2000 | 0
12 | 2000 | 0
13 | 2000 | 0
14 | 2000 | 0
15 | 2000 | 0
16 | 2000 | 0
17 | 2000 | 0
18 | 2000 | 0
19 | 2000 | 0
20 | 2000 | 0
21 | 2000 | 0
22 | 2000 | 0
23 | 2000 | 0
24 | 2000 | 0

## Slide 8: Proposed Non-Spin Methodology Examples – May ‘11
Current Methodology
Proposed Methodology
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 1716 | -2
2 | 1716 | -2
3 | 1539 | 0
4 | 1539 | 0
5 | 1539 | 0
6 | 1539 | 0
7 | 1597 | 0
8 | 1597 | 0
9 | 1597 | 0
10 | 1597 | 0
11 | 1942 | -362
12 | 1942 | -362
13 | 1942 | -362
14 | 1942 | -362
15 | 2000 | -406
16 | 2000 | -406
17 | 2000 | -406
18 | 2000 | -406
19 | 2000 | -375
20 | 2000 | -375
21 | 2000 | -375
22 | 2000 | -375
23 | 1716 | -2
24 | 1716 | -2
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 1570 | 0
2 | 1570 | 0
3 | 1497 | 0
4 | 1497 | 0
5 | 1497 | 0
6 | 1497 | 0
7 | 1494 | 0
8 | 1494 | 0
9 | 1494 | 0
10 | 1494 | 0
11 | 2000 | -382
12 | 2000 | -382
13 | 2000 | -382
14 | 2000 | -382
15 | 2000 | -430
16 | 2000 | -430
17 | 2000 | -430
18 | 2000 | -430
19 | 2000 | -148
20 | 2000 | -148
21 | 2000 | -148
22 | 2000 | -148
23 | 1570 | 0
24 | 1570 | 0

## Slide 9: Proposed Non-Spin Methodology Examples – July ‘11
Current Methodology
Proposed Methodology
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 1237 | 0
2 | 1237 | 0
3 | 1663 | 0
4 | 1663 | 0
5 | 1663 | 0
6 | 1663 | 0
7 | 1947 | 0
8 | 1947 | 0
9 | 1947 | 0
10 | 1947 | 0
11 | 1399 | -399
12 | 1399 | -399
13 | 1399 | -399
14 | 1399 | -399
15 | 2000 | -645
16 | 2000 | -645
17 | 2000 | -645
18 | 2000 | -645
19 | 2000 | -645
20 | 2000 | -645
21 | 2000 | -645
22 | 2000 | -645
23 | 1237 | 0
24 | 1237 | 0
IE | NSRS Requirement | Net Error Subtracted from Load Forecast
1 | 1527 | 0
2 | 1527 | 0
3 | 1836 | 0
4 | 1836 | 0
5 | 1836 | 0
6 | 1836 | 0
7 | 1532 | -50
8 | 1532 | -50
9 | 1532 | -50
10 | 1532 | -50
11 | 1999 | -834
12 | 1999 | -834
13 | 1999 | -834
14 | 1999 | -834
15 | 2000 | -637
16 | 2000 | -637
17 | 2000 | -637
18 | 2000 | -637
19 | 2000 | -421
20 | 2000 | -421
21 | 2000 | -421
22 | 2000 | -421
23 | 1527 | 0
24 | 1527 | 0