| NOGRR Number | 074 | NOGRR Title | Clarified Responsible Entities for Reporting Sabotage Information to NERC |
| --- | --- | --- | --- |

| Date | September 26, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | DeAnn Walker |
| E-mail Address | deann.walker@centerpointenergy.com |
| Company | CenterPoint Energy Houston Electric, LLC |
| Phone Number | 512-397-3032 |
| Cell Number | 512-784-0998 |
| Market Segment | Investor Owned Utility |

Comments

The language proposed by the various comments impose reporting requirements on utilities for systems for which reporting is not currently required.  The reporting requirements should not be expanded.  Therefore, CenterPoint Energy proposes language that will apply to the systems and occurrences applicable under the North American Electric Reliability Corporation (NERC) Standards, instead of expanding the applicability.

Revised Proposed Guide Language

3.7.3	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the Rating of their Facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA Rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this Rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA Rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this Rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA Rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this Rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This Rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these Ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Elements to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 3.8	Requirements for Reporting Sabotage Information

(1)	An ERCOT-registered Entity that is required to develop procedures to report an act of sabotage pursuant to the applicable North American Electric Reliability Corporation (NERC) standards shall notify ERCOT, by phone or email at shiftsupervisors@ercot.com, when acts covered by such procedures occur in the ERCOT Region.  Transmission Service Providers (TSPs) and Resource Entities may designate their Transmission Operators (TOs) or Qualifed Scheduling Entities (QSEs) to notify ERCOT of the event, provided that no TO or QSE may be compelled to undertake the reporting for another ERCOT-registered Entity.

(2)	ERCOT shall inform NERC and other governmental agencies of the threat of sabotage in accordance with current NERC Reliability Standards, laws, and regulations on behalf of the ERCOT Entities that report sabotage to ERCOT.

(3)	ERCOT shall communicate information regarding the sabotage event to appropriate Entities within the ERCOT Region on behalf of the Resource Entities, TSPs, TOs and QSEs.