## Slide 1: A Review of ERCOT’s NSRS Study
RDTF
September 23, 2011

## Slide 2: ERCOT’s NSRS Analysis
ERCOT Analysis:
Analyzed only the deployment intervals in which load exceeded the load at the time of the deployment
This assumes that prices will converge to the proposed floor
Subtracted the actual observed price from the proposed floor and added the difference to PNM. If difference was negative then added zero
Assumed varying fixed horizontal price floors as a proxy to represent online and offline resource offer floors as described in their proposals
ERCOT had a limited amount of time to perform their analysis and utilized a number of simplistic assumptions that appear to materially overstate the impact of the proposals.
2

## Slide 3: Areas of Needed Refinement
More precise determination of when NSRS will actually set clearing price
Accurate representation of sloped offer floors
Account for the fact that the minimum block (i.e.; capacity up to LSL) of deployed NSRS will not set clearing price
Perform sensitive analysis of:
  The 1,000 MW of offline NSRS that structurally moved to the Quick Start NSRS category beginning in July
  Weather normalization – what might the typical year impact of the Compromise Proposal be?
To provide the level of policy maker insight required for this decision, a more sophisticated approach is required.
3

## Slide 4
4
Represents what ERCOT approach yielded
Represents impacts of potential over statements of ERCOT technique
Represents impacts of potential sensitivities that need to be performed
A
B
A Walk Forward From ERCOT’s Analysis
This illustrates how important it is to take ERCOT’s analysis to the next level of sophistication, so that policy makers will fully understand the expected impacts of the proposals.
Note: the analysis presented in this slide was calculated using the data available to Luminant and could be refined and improved by utilizing ERCOT’s more complete dataset.
C
$154k
$77k
$27k
$16k
$5k
B
C
$127k
$22k

## Slide 5: 1. When does NSRS set clearing price?
ERCOT’s analysis did not utilize the actual SCED Up or HDL to determine when NSRS units would actually be “on the margin”
ERCOT’s approach overstated pricing impact of NSRS deployments because it did not account for changing supply across NSRS deployment intervals
  Varying wind output; thermal gen returning from forced outage, etc…
5
NSRS deployments can only set clearing price when the energy offer curves from this deployed capacity are the incremental energy being deployed by SCED.

## Slide 6
On June 27, 2011, the ERCOT approach may have overstated the time where NSRS could have set price by ~90 minutes (i.e. 1 ½ hours) compared to the SCED Up approach
6
1. When does NSRS set clearing price?
Time Period of NSRS Impact by ERCOT Analysis
More Accurate Time Period of NSRS Impact

## Slide 7
On August 4, 2011, the ERCOT approach may have overstated the time where NSRS could have set price by ~30 minutes compared to the SCED Up approach.
7
1. When does NSRS set clearing price?
Time Period of NSRS Impact by ERCOT Analysis
More Accurate Time Period of NSRS Impact

## Slide 8
On February 9, 2011, the ERCOT approach may have overstated the time where NSRS could have set price by ~330 minutes (i.e. 5 ½ hours) compared to the SCED Up approach.
8
1. When does NSRS set clearing price?
Time Period of NSRS Impact by ERCOT Analysis
More Accurate Time Period of NSRS Impact Would Be Zero (green line always above blue line)

## Slide 9
On February 2-4, 2011, the ERCOT approach dramatically overstated the time where NSRS could have set price. This one event resulted in a 15% increase of PNM in their analysis.
9
1. When does NSRS set clearing price?
Time Period of NSRS Impact by ERCOT Analysis
More Accurate Time Period of NSRS Impact Would Be Only In These Ellipses

## Slide 10: 2. Sloped offer floors
10
The sloped offer floors of the Compromise Proposal, will likely result in a lower impact to clearing prices than a horizontal offer floor approach as assumed in ERCOT’s analysis.

## Slide 11: 3. Minimum Block Impact on Prices
11
Only the Energy Offer Curve (e.g. LSL to HSL) portion of the NSRS deployment can set the clearing price. Whereas, the Minimum Block (0 to LSL MW) can not.

## Slide 12
June 27, 2011, using SCED Up and considering LSL price taking MWs, 2 ¼ hrs of NS setting price.
12
Price taking impact of LSL for QS & Offline NS

## Slide 13
13
Without LSL impact (from slide 6)

## Slide 14: 4a. Offline to QS Structural Change
14
A sensitivity that considers the structural move of 1,000 MW from Offline to Quick Start NSRS beginning in July is relevant for this decision, if it is expected to be a durable change.

## Slide 15
15
Represents what ERCOT approach yielded
Represents impacts of potential over statements of ERCOT technique
Represents impacts of potential sensitivities that need to be performed
A
B
A Walk Forward From ERCOT’s Analysis
This illustrates how important it is to take ERCOT’s analysis to the next level of sophistication, so that policy makers will fully understand the expected impacts of the proposals.
Note: the analysis presented in this slide was calculated using the data available to Luminant and could be refined and improved by utilizing ERCOT’s more complete dataset.
C
$154k
$77k
$27k
$16k
$5k
B
C
$127k
$22k

## Slide 16: 4b. Weather Normalization of NSRS
16
Although NSRS procurement methodologies have varied since market open1, a review of the deployments by year is instructive when attempting to weather normalize 2011.
1): The NSRS Procurement Methodology has remained approximately the same for 2010 and 2011.

## Slide 17: Recommendation
We believe these factors should be corrected and the analysis should be further refined to ensure pricing impacts are adequately estimated
Results of the study are critical in providing proper price to incentivize generation investment in ERCOT
17