| NOGRR Number | 074 | NOGRR Title | Clarified Responsible Entities for Reporting Sabotage Information to NERC |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | September 1, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Sections Requiring Revision |  | 3.7.3, ERCOT Requirements for Reporting Sabotage Information (delete) 3.7.4, Responsibility for Equipment Ratings 3.8, Requirements for Reporting Sabotage Information (new) |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds Entities responsible for notifying the North American Electric Reliability Corporation (NERC) or other governmental agencies of a threat of sabotage. |  |  |
| Reason for Revision |  | Transmission Service Providers (TSPs), Qualified Scheduling Entities (QSEs) and other registered Entities are currently required to report experiences of disturbances or unusual occurrences suspected or determined to be caused by sabotage as described in the NERC Reliability Standards. For consistency, this NOGRR would require those Entities to also report any threat of sabotage. |  |  |
| Overall Market Benefit |  | Clarifies responsibilities for reporting threat of sabotage. |  |  |
| Overall Market Impact |  | Unknown. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Procedural History |  | - On 5/18/11, NOGRR074 was posted. - On 6/14/11, CenterPoint Energy comments were posted. - On 6/15/11, the Operations Working Group (OWG) considered NOGRR074. - On 7/11/11, an Impact Analysis was posted. - On 7/20/11, the OWG considered the 6/15/11 OWG Report and Impact Analysis for NOGRR074. - On 8/11/11, ROS considered NOGRR074. - On 8/23/11, ERCOT comments were posted. - On 8/31/11, TMPA comments were posted. - On 9/1/11, TAC considered NOGRR074. |  |  |
| OWG Decision |  | On 6/15/11, OWG was in consensus to recommend approval of NOGRR074 as amended by the 6/14/11 CenterPoint Energy comments and as revised by OWG. On 7/20/11, OWG was in consensus to endorse and forward the 6/15/11 OWG Report and Impact Analysis for NOGRR074 to ROS. |  |  |
| Summary of OWG Discussion |  | On 6/15/11, OWG was in agreement to further clarify the responsibilities of Entities reporting sabotage. On 7/20/11, there was no discussion. |  |  |
| ROS Decision |  | On 8/11/11, ROS unanimously voted to recommend approval of NOGRR074 as recommended by OWG in the 7/20/11 OWG Report. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 8/11/11, there was no discussion. |  |  |
| TAC Decision |  | On 9/1/11, TAC unanimously voted to table NOGRR074 for one month. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 9/9/11, participants agreed to table NOGRR074 for one month to allow additional time to review and address any compliance concerns. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clarifies responsibilities for reporting threat of sabotage. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Frank Owens on Behalf of the Nodal Protocol and Guides Resolution Task Force (NPGRTF) |
| E-mail Address | fowens@texasmpa.org |
| Company | Texas Municipal Power Agency |
| Phone Number | 936-873-1120 |
| Cell Number | 979-204-7725 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sonja B. Mingo |
| E-Mail Address | smingo@ercot.com |
| Phone Number | 512-248-6463 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| CenterPoint Energy 061411 | Proposed rejection of NOGRR074 or deletion of redundant language requiring Entities to comply with the NERC Reliability Standards |
| ERCOT 082311 | Capitalized define terms and corrected grammatical errors. |
| TMPA 083111 | Provided clarifying language for Facilities associated with the ERCOT System. |

Proposed Guide Language Revision

3.7.3	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Elements to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 3.8	Requirements for Reporting Sabotage Information

(1)	ERCOT-registered Entities or their Designated Agent shall notify ERCOT, by phone or email at shiftsupervisors@ercot.com, when disturbances or unusual occurrences are suspected or determined to be caused by sabotage and shall have procedures for the recognition of sabotage events at its facilities.

(2)	ERCOT shall inform the North American Electric Reliability Corporation (NERC) and other governmental agencies of the threat of sabotage in accordance with current NERC Reliability Standards, laws, and regulations.  ERCOT may inform other ERCOT-registered Entities of the event(s), if, in the opinion of ERCOT, the situation impacts ERCOT System reliability.