ERCOT Operations Report

Sep 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 9/2/2011 21:56 | 59.873 | 258 | Gen Deviation -1700 MW in 4 mins. Out of URS. |
| 9/3/2011 0:11 | 59.899 | 32 | Gen Deviation -2500 MW in 6 mins. |
| 9/4/2011 0:09 | 59.885 | 64 | Gen Deviation -1500 MW in 2 mins. Out of URS. |
| 9/4/2011 3:43 | 59.861 | 20 | Unit trip with 545 MW online. |
| 9/4/2011 10:12 | 59.822 | 69 | Unit trip with 832 MW online. |
| 9/6/2011 4:41 | 59.799 | 140 | Unit trip with 817 MW online. |
| 9/6/2011 15:47 | 59.884 | 16 | Unit trip with 600 MW online. |
| 9/13/2011 21:58 | 59.898 | 16 | Gen Deviation -1200 MW in 3 mins. Out of URS |
| 9/19/2011 1:35 | 59.755 | 102 | Unit trip with 811 MW online. |
| 9/25/2011 23:04 | 59.861 | 171 | Gen Deviation -1700 MW in 3 mins. Out of URS. |
| 9/28/2011 12:28 | 59.872 | 40 | Unit trip with 586 MW online. |
| 9/30/2011 12:03 | 59.855 | 52 | Unit trip with 700 MW online. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 9/2/11 21:56:07 | 9/2/11 22:01:37 | 0:05:30 | 626.9 |  |
| 9/3/11 0:11:16 | 9/3/11 0:13:52 | 0:02:36 | 450.6 |  |
| 9/4/11 0:09:16 | 9/4/11 0:13:40 | 0:04:24 | 548.2 |  |
| 9/4/11 3:43:32 | 9/4/11 3:46:08 | 0:02:36 | 318.6 |  |
| 9/4/11 10:12:44 | 9/4/11 10:15:48 | 0:03:04 | 475.9 |  |
| 9/6/11 4:41:32 | 9/6/11 4:48:16 | 0:06:44 | 825.8 |  |
| 9/6/11 15:46:08 | 9/6/11 15:49:40 | 0:03:32 | 567.9 |  |
| 9/13/11 21:58:04 | 9/13/11 22:01:42 | 0:03:38 | 476.7 |  |
| 9/19/11 1:35:26 | 9/19/11 1:38:54 | 0:03:28 | 1086.5 |  |
| 9/25/11 23:03:56 | 9/25/11 23:08:00 | 0:04:04 | 654.9 |  |

RUC Capacity Purchases

| Weather Zone | Unit Days |
| --- | --- |
| COAST | 25 |
| EAST | 6 |
| NORTH CENTRAL | 16 |
| SOUTH | 2 |
| SOUTH CENTRAL | 13 |
| Grand Total | 62 |

SCED Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 21 |
| DCKT Roansprairie - Kuykendahl-King & Singleton -Tomball 345 kV | Singleton - Zenith 345 kV | 14 |
| Basecase | Golden Switch - Brand (Oncor) 138 kV | 9 |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Fayette XFMR 6at2 345/138 kV | 8 |
| DCKT Greens Bayou - Gable & Hardy - Crocket 138 kV | Garrott - Midtown 138 kV | 8 |
| Paloduro Sub - Pearsall Switching Station 138 kV | Pearsall Switching Station 138/69 kV XFMER | 8 |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Columbus - Stafford 69 kV | 6 |
| Basecase | Whirlwind XFMR1 | 6 |
| Elm Mott - Tradinghouse SES 345 kV | Bosque Switch - Rogers Hill 138 kV | 6 |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Flatonia - Halletsville 138 kV | 5 |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Winchester - Smithville 138 kV | 5 |
| Fayette Plant 2 - Lytton Springs & Holman AEN 345 kV | Bell South - Peters 138 kV | 5 |
| Caney Creek - Dyann 138 kV | Lane City - Blessing 138 kV | 5 |
| Crane Arco Tap - Pleasant Farms Tap 138 kV | Fort Stockton Switch - Barilla 69 kV | 5 |
| Scurry Switch - Sun Switch 138 kV | Spur - Aspermont 138 kV | 4 |
| Cagnon 345/138 kV XFMR1 | Cagnon 345/138 kV XFM4H | 4 |
| Bluff Creek 345/138 kV Transformer 2 | Oak Creek CSW - Nicole 138 kV | 4 |
| Paint Creek - Aspermont 138 kV | Aspermont 138/69 kV XFMR1 | 4 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North - North Cowden 69 kV | 3 |
| DCKT STP - DOW 345 kV | STP - Hillje 345 kV | 3 |
| STP - Blessing 345 kV | Columbus - Stafford 69 kV | 3 |
| DCKT Elmcreek - Hill Country & Skyline 345 kV | Marion - Skyline 345 kV | 3 |
| Rodd Field - Barney Davis 138 kV | Airline - Cabaniss 138 kV | 3 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69 kV | 3 |
| DCKT Nueces Bay - Koch Up River & Lon Hill 138 kV | Hiway - Air Liquide 69 kV | 3 |
| DCKT Roansprairie - Kuykendahl-King & Singleton -Tomball 345 kV | Singleton - Zenith 345 kV (other line) | 2 |
| DCKT Roansprairie - Kuykendahl-King & Singleton -Tomball 345 kV | Jewett - Rattlesnake Rd Switch 345 kV | 2 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - BTU Jack Creek Switch 345 kV | 2 |
| Cabaniss - Airline CSW 138 kV | Barney Davis - Rodd Field 138 kV | 2 |
| DCKT Watermill - Tricorner & Trinidad SES 345 kV | Segoville Switch - Kleberg Tap 138 kV | 2 |
| Laquinta - Lobo 138 kV | Falfurias - Premont 69 kV | 2 |
| San Angelo Red Creek - Comanche Switch 345 kV | Flat Creek - Leon Switch 138 kV | 2 |
| DCKT Roansprairie - Kuykendahl-King & Singleton -Tomball 345 kV | Garrott - Midtown 138 kV | 1 |
| Caney Creek - Dyann 138 kV | Altair - Stafford 69 kV | 1 |
| Caney Creek - Dyann 138 kV | Lane City - New Gulf 138 kV | 1 |
| Caney Creek - Dyann 138 kV | Rogers Hill - Elm Mott 138 kV | 1 |
| Caney Creek - Dyann 138 kV | Aspermont 138/69 kV XFMR1 | 1 |
| Caney Creek - Dyann 138 kV | Cagnon 345/138 kV XFM4H | 1 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Gibbons Creek 345 kV | 1 |
| DCKT Jewett - Singleton 345 kV | Gibbons Creek - Singleton 345 kV | 1 |
| DCKT Graham - Long Creek 345 kV | Putnam 138/69 kV XFMR | 1 |
| DCKT Graham - Long Creek 345 kV | Murray - Paint Creek 138 kV | 1 |
| DCKT Austrop - Lost Pines 345 kV | Fayette Plant 1 - Fayette Plant 2 | 1 |
| DCKT Austrop - Lost Pines 345 kV | Austrop 345/138kV AT1 | 1 |
| Lobo - San Miguel 345 kV | Laquinta - Lobo 138 kV | 1 |
| San Miguel - San Miguel Switch 138 kV | Pearsall - Paloduro Sub 138 kV | 1 |
| DCKT STP - Hillje & Elmcreek 345 kV | STP - Hillje 345 kV | 1 |
| DCKT Tradinghouse SES - Venus Switch 345 kV | Jewett - Rattlesnake Rd Switch 345 kV | 1 |
| San Angelo Red Creek - Twinbute 345 kV | Twinbute 345/138 kV XFMR1L | 1 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 1 |
| Ingleside Du Pont - Ingleside Cogenswitch 138 kV | Ingleside Du Pont - Du Pont Switch Ingleside 138 kV | 1 |
| DCKT Sim Gideon - Bastwe & Lockhart 138 kV | Zorn - Poolro 138 kV | 1 |
| Air Liquid AEP - Valero East 69 kV | Kochup River 138/69 kV AXFMR | 1 |
| China Grove Switch - Bluff Creek Switch 138 KV | Golden Switch - Brand (Oncor) 138 kV | 1 |
| Citgo North - Hiway 9 138 kV | Nueces Bay - Hiway 9 138 kV | 1 |
| Barilla 138/69 kV XFMR | Alamito Creek 138/69 kV XFMR | 1 |
| Oklaunion - Abilene Mulberry Creek 345 kV | Fisher Road Switch - Wichita Falls 138 kV | 1 |
| Crestonio - Falfurias 138 kV | San Diego - Freer 69 kV | 1 |
| Formosa - Lolita 138 kV | Victoria - Victoria Du Pont Switch 138 kV | 1 |
| Bluff creek Switch - Exxon Sharon Ridge 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| DCKT Ball Park - JT Deely & JT Dee 138 kV | Caleveras - Streich 138 kV | 1 |
| Green Mt - Parkway & Skyline 138 kV | Skyline - Nacogdoches 138 kV | 1 |
| Formosa 138/69 kV XFMR TR22 | Formosa 138/69 kV XFMR TR21 | 1 |
| Lytton Springs 345/138 kV AXFMR #2 | Lytton Springs 345/138 kV AXFMR #1 | 1 |
| Moss Switch - Westover 138 kV | Moss Switch - Amoco North Cowden Tap 138 kV | 1 |
| DCKT Royse Switch - Allen Switch 345 kV | Apollo - Richardson east 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 11 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 09/01/2011 | Transmission and Security Desk V1 Rev10 | 556 |
| 09/01/2011 | Shift Supervisor Desk V1 Rev7 | 555 |
| 09/01/2011 | Resource Desk V1 Rev9 | 554 |
| 09/01/2011 | Reliability Unit Commitment Desk V1 Rev9 | 553 |
| 09/01/2011 | Real Time Desk V1 Rev10 | 552 |
| 09/01/2011 | DC Tie Desk V1 Rev8 | 551 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

09/03 17:00 63,135 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | 3.46 |
| March | 3.29 | 3.24 | 2.24 | 2.02 |
| April | 2.45 | 2.66 | 2.47 | 3.55 |
| May | 3.01 | 2.90 | 2.63 | 3.27 |
| June | 2.81 | 2.89 | 2.84 | 2.28 |
| July | 2.55 | 2.83 | 2.39 | 1.63 |
| August | 3.66 | 3.07 | 2.29 | 2.28 |
| September | 4.99 | 3.68 | 3.14 | 2.70 |
| October | 2.79 | 2.92 | 2.37 | NA |
| November | 2.60 | 1.93 | 3.46 | NA |
| December | 4.54 | 3.70 | 2.60 | NA |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.68 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 9/1/2011 | 11:36 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 13:00 19:00 |
| 9/1/2011 | 15:29 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/1/2011 | 22:35 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/2/2011 | 00:42 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/2/2011 | 01:49 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1500 2100 |
| 9/2/2011 | 12:29 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/6/2011 | 15:50 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/10/2011 | 12:34 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/11/2011 | 13:06 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 18:00 |
| 9/11/2011 | 13:50 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/12/2011 | 16:02 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/12/2011 | 19:00 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/13/2011 | 03:10 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 18:00 |
| 9/18/2011 | 13:43 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/20/2011 | 17:13 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/21/2011 | 15:06 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/22/2011 | 20:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/23/2011 | 15:53 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/24/2011 | 22:15 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/25/2011 | 10:10 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 19:00 |
| 9/25/2011 | 17:10 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/26/2011 | 15:31 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/27/2011 | 03:25 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 18:00 |
| 9/28/2011 | 15:50 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 9/29/2011 | 11:10 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 17:00 |
| 9/29/2011 | 12:33 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 17:00 |
| 9/30/2011 | 15:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 19:00 |
| 9/30/2011 | 23:22 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

None

Emergency Notice

None

Texas RE Event Analysis

None