## Slide 1: PDCWG Report to ROS
October 13, 2011
Sydney Niemeyer

## Slide 2: ERCOT Frequency Control Performance
September, 2011

## Slide 13: NERC Frequency Response Field Trial

## Slide 14: NERC BAL-003 Field Trial
Sets Interconnection minimum frequency response.
  Goal to prevent activation of UFLS for the largest N-2 event 2750 MW.
  Present recommendation for Texas is minimum of -286 MW/0.1 Hz measured at Point B.
    2750 – 1150 = 1600 MW/(-0.600 x 10) = -266 MW/0.1 Hz.

## Slide 15: September 28, 2011 PDCWG Open Meeting
Review of 20% limit of RRS based on Generator Capacity (HSL).
Discussed history of limit.
  Primary Frequency Response (Droop) of 5% will cause the Governor to move 20% of the output of the generator with a -0.600 Hz change in frequency.
  Distributes reserves on multiple generators to improve Interconnection frequency response and deliverability of reserves.
  80% loading point on traditional steam turbines had the lowest average heat rate.

## Slide 16: Historical Performance
May 15, 2003 event where frequency declined to 59.261 Hz.
  From 60.012 to 59.297 in 4.5 seconds.
  How much energy can a traditional generator deliver in 4.5 seconds?
    1511 MW from turbines.
    475 MW from load dampening.
    471 MW from LaaR
    979 MW from Firm Load. (first event)

## Slide 17: Today: Increased Load Resources and More Turbine Response
  How much energy can a traditional generator deliver in 4.5 seconds?
    1811 MW from turbines (for same 3434 MW loss)
    475 MW from load dampening.
    1150 MW from LaaR
    0 MW from Firm Load
  For 2750 MW event instead of 3434 MW
    1127 MW from turbines.

## Slide 18
May 15, 2003 Actual Performance

## Slide 19
May 15, 2003 02:53

## Slide 20: If the % of RRS Was Changed
Expected Primary Frequency Response from RRS providers if all capacity is frequency responsive.

## Slide 21: To Prevent UFLS

## Slide 22: Is 20% the Right Amount?
Increasing % allowed to be provided by a single Resource would decrease PFR.
  Increase risk of UFLS.
  Governor can not move Gen full % before UFLS.
Decreasing % allowed to be provided by a single Resource would increase PFR.
  Decrease risk of UFLS.
  Easier for Generator to perform.
No change in %. Continue effort to improve PFR from RRS providers.
  Continue to expect PFR from all spinning reserve and improve their performance.

## Slide 23: Find Other Sources of PFR
Short duration, fast response (less than 4 seconds) would decrease the risk of UFLS.
  Storage
  Flywheel
Create a Product for this service.

## Slide 24: Recent Frequency Response Performance

## Slide 27
Higher frequency rate of change per MW tripped than the May 15, 2003 event.

## Slide 28: PDCWG On-going Work
Continue review of Generator’s Primary Frequency Response Performance.
  Contacting low performers to help improve performance.
  Observed PFR from two wind farms during minor high frequency following unit trips.
Continue effort to review protocols and guides to clarify PFR and RRS responsibilities.