## Slide 1: SCED Overview and Results
Chad Thompson, ERCOT
Special ROS PGRR011 Workshop
October 21st, 2011

## Slide 2: Presentation Outline
Real-Time Congestion Management
  Overview
  What Contingencies/Constraints are Considered?
Constraints Irresolvable by SCED
  Actions Used to Maintain System Security
  Constraints Consistently Irresolvable by SCED
  Irresolvable by SCED vs. N-1 Insecure
  Settlements
Responses to ROS Comments
Additional Questions

## Slide 3: Real-Time Congestion Management Overview
The Security Constrained Economic Dispatch (SCED) is simply one component of the process through which Generation Resources are dispatched based on current system conditions
Other components of the process include:
  SCADA Telemetry
  State Estimator
  Network Security Analysis (NSA)
  Transmission Constraint Manager (TCM)
  Resource Limit Calculator (RLC)

## Slide 4: Real-Time Congestion Management Overview
The NSA and the TCM both play a major role in real-time congestion management
The NSA analyzes contingencies to monitor for potential system element exceedances
The NSA then passes information to the TCM for constraints that may need some action by the Operator
  For example, if a constraint is resolved by a RAP or SPS, that constraint will not be passed to the TCM
Using the TCM interface, the Operator is able to select the constraints that will be sent to SCED for consideration during the next SCED execution
  A constraint is defined by a contingency and an overloaded element

## Slide 5: What Contingencies/Constraints are Considered?
The following guidelines are used in determining which contingencies are considered in the real-time process:
  ERCOT models all single transmission line, autotransformer, and generation unit contingencies
    This is performed using an automatic contingency generator application developed by the ERCOT Network Modeling Department and has been discussed with the Network Data Support Working Group (NDSWG)
  Certain additional contingencies are defined manually in the CIM where the automatic contingency generator cannot be used
    Double-Circuits
      Modeled based on information received by Transmission Owners (discussed in previous NDSWG meetings)
    Multi-unit contingencies such as whole combined-cycle trains
    Additional multi-unit contingencies are modeled pursuant to ERCOT and NERC requirements (e.g. double STP or Comanche Peak)

## Slide 6: What Contingencies/Constraints are Considered?
The SCED process is then executed to produce Resource-specific base point instruction and LMPs
Only the transmission constraints that were activated in the TCM will considered by SCED
There are three potential states for transmission constraints following a SCED execution
The constraint can be:
  Not binding
  Binding
  Violated
For a violated constraint, the shadow price will be equal to the shadow price cap

## Slide 7: Actions Used to Maintain System Security
There may be cases in which the SCED process is not able to resolve a constraint
Nodal Protocol 6.5.7.1.10(3) describes actions that ERCOT may take in real-time to relieve any issues
Additional tools available to the ERCOT Operator include Mitigation Plans (MPs) and Temporary Outage Action Plans (TOAPs), in the event a contingency occurs in real-time
  These can be implemented in concert with utilizing SCED to manage congestion
  Constraints with generator shift factors greater than 2 % will still be activated in SCED
ERCOT has been able to manage congestion, ensure grid reliability, and maintain compliance with applicable NERC Reliability Standards

## Slide 8: Constraints Consistently Irresolvable by SCED
The ERCOT Business Practices Document “Setting the Shadow Price Caps and Power Balance Penalties in Security Constrained Economic Dispatch” was presented to the Technical Advisory Committee (TAC) at its October 11 Special Meeting, and was recommended for approval by the Board of Directors
Under Section 3.6.1, the shadow price cap for a non-competitive constraint will be modified once one of the following conditions is met:
  A non-competitive constraint violation is not resolved by the SCED dispatch or overridden for more than two consecutive hours on more than four consecutive Operating Days; or
  A non-competitive constraint violation is not resolved by the SCED dispatch for more than a total of 20 hours within a rolling thirty day period

## Slide 9: Constraints Consistently Irresolvable by SCED
After one of the trigger conditions is met, the shadow price cap for the constraint is calculated based on the Business Practices Document
Based on the analysis provided at the October 11 TAC meeting, a list of seven potential constraints for which the shadow price cap may be modified was identified
Unless modified per the Business Practices Document, the shadow price cap for a transmission constraint is set using one of the following generic values:
  345 kV -- $4,500
  138 kV -- $3,500
  69 kV -- $2,800
  Base Case / Generic Constraints -- $5,000

## Slide 10: Irresolvable by SCED vs. N-1 Insecure
SCED Irresolvable refers to congestion which cannot be alleviated due to inability of SCED to dispatch Resources past a certain threshold (max shadow price)
  Could be due to factors such as ramp rate limitations or economics of the capable resources
N-1 Secure refers to the ability of the ERCOT ISO to withstand the loss of a credible single contingency without exceeding or violating System Operating Limits or Interconnection Reliability Operating Limits
SCED Irresolvable is not typically the result of an N-1 insecure state
  When ERCOT is N-1 insecure, it will issue a transmission watch

## Slide 11: Settlements
ERCOT is drafting material regarding settlements and will post an updated presentation when completed

## Slide 12: Responses to ROS Comments
Would changing SCED so that it only changes generator outputs after a contingency actually occurs rather than before a contingency occurs address most of the gaps between planning and operating processes?
  This implies SCED only dispatches generation for power balance and base case (N-0) constraints, and might require additional Protocol changes to implement
    Economically, that would set the default max shadow price for all constraints to $5,000 since every constraint would be base case
  Due to ramp rate limitations, SCED might not be able to redispatch generation post-contingency to resolve an overload
    As indicated earlier (slide 10), ramp rate restrictions could cause equipment damage as a result of SCED being unable to resolve an overload in time.

## Slide 13: Responses to ROS Comments
Would changing SCED so that it only changes generator outputs after a contingency actually occurs rather than before a contingency occurs address most of the gaps between planning and operating processes?
  This change may impact compliance with NERC Reliability Standards
    ERCOT is required to respect System Operating Limits and Interconnection Reliability Operating Limits both pre- and post-contingency

## Slide 14: Responses to ROS Comments
How does ERCOT Operations respond to irresolvable SCED solutions?
  The details of the actions taken by ERCOT grid operators to manage potential SCED irresolvable constraints can be found in Section 4.1 of the ERCOT Transmission and Security Desk Procedure
    http://www.ercot.com/mktrules/guides/procedures/index
  The Operations Support Staff may also work with affected Transmission Owners to develop a RAP, MP, PCAP, or TOAP to maintain grid reliability in the event the contingency occurs

## Slide 15: Responses to ROS Comments
Questions were also generally raised about the 1200 irresolvable SCED intervals that were presented
  Proper context is needed
  The data presented was approximately 1184 settlement intervals where the max shadow price was experienced
  Multiple constraints at the max shadow price for the same settlement interval were counted twice
  Comparing the number of settlement intervals where the max shadow price was experienced to the total number of binding settlement intervals:
    1184 settlement intervals at max shadow price
    25459 total binding intervals
    1184 / 25459 = ~4.65 %

## Slide 16: Responses to ROS Comments
Questions were also generally raised about the 1200 irresolvable SCED intervals that were presented
  ERCOT analyzed congestion Nodal-to-Date (10/5/11) pursuant to Section 3.6.1 of the ERCOT Business Practices Document (Slide 8), and identified only 7 constraints meeting the criteria
Constraint Name | Description
SKEYWLV8_6611__C | Loss of Willow Valley – Lamesa 138 kV overloads Ackerly Lyntegar – Sparenburg 69 kV
SNCWHLT9_6915__A | Holt Switch – Odessa North 69 kV overloads Odessa North – Odessa Basin Switch 69 kV
DW_DDEN8_AIR_W_DE_1 | Denton Steam – Argyle / West Denton 138 kV overloads West Denton – Jim Christal 138 kV
DODEQAL5_6611__A | Odessa Switch – Quail Switch / Longshore Switch 345 kV overloads Ackerly Vealmoor Switch – Ackerly 69 kV
SCABWES8_NAVAL__N_PADR1_1 | AEP Airline – AEP West Side 138 kV overloads Naval Base – North Padre 69 kV
SNCWMOS8_ODNTH_FMR1 | Holt Switch – Moss Switch 138 kV overloads the Odessa North 138/69 kV Auto # 1
BASE CASE_VALIMP | Valley Import Voltage Stability Generic Transmission Limit

## Slide 17: Responses to ROS Comments
Details on the 7 Potential SCED Irresolvable Constraints
  The Valley Import constraint is the only qualifying SCED Irresolvable constraint attributed to a base case System Operating Limit exceedance
  Two constraints are based on double-circuit contingencies
    DW_DDEN8_AIR_W_DE_1
    DODEQAL5_6611__A
  Preliminary assessment of the constraints:
    Four are due to local congestion in West Texas for which there are few generators with significant shift factors to resolve the congestion
    One is due to local congestion in the DFW area around the time of the Cold Weather Event in February.
    One is due to a small load pocket near Corpus Christi
    One is the Valley Import Voltage Stability Limit

## Slide 18: Responses to ROS Comments
Details on the 7 Potential SCED Irresolvable Constraints
  An MP was developed for the Valley Import
  TOAPs were developed for the Odessa North Auto, West Denton – Jim Christal, and Ackerly Lyntegar – Sparenburg constraints
    Ackerly Lyntegar – Sparenburg TOAP would work for the Ackerly Vealmoor – Ackerly line, but a TOAP was never implemented for the constraint

## Slide 19: Responses to ROS Comments
Any additional information to support a gap?
  The ERCOT Interconnection has not exhibited any grid-wide cascading outages as a result of a forced outage
  ERCOT has experienced several operational events, but no grid damage has been observed outside the local areas affected by them
    The February 2, 2011 extreme weather event
    The contamination issues as a result from the recent draught and wildfires

## Slide 20: Responses to ROS Comments
Do NERC requirements prevent operating the transmission system such that generation adjustments are made after a contingency occurs rather than before?
  The NERC Reliability Standards do not necessarily prevent operating the grid to move generation post-contingency, however ERCOT is required to respect its System Operating Limits and Interconnection Reliability Operating Limits both pre- and post-contingency
  ERCOT is working on implementing a Dynamic Remedial Action Plan program within the Network Security Analysis which may allow for dispatching generation post-contingency through SCED

## Slide 21
Additional Questions?