## Slide 1: Reliability Requirements
Bill Blevins
Manager of Operations Support
ERCOT

## Slide 2: Operating Security Limit to SOLs and IROLs
Operating Limit Definition Task Force (OLD-TF) in November 2002
In March 2003 the OLD-TF submitted a report to the Operating
Committee suggesting that there were, in fact, two types of Operating Security Limit violations:
1. Those that would affect only a “limited set of facilities” were
called System Operating Limits (SOL), and
2. Those that posed a serious threat to the reliability of the bulk
power system, such as instability, uncontrolled loss of
Interconnection integrity, or voltage collapse, were called
Interconnection Reliability Operating Limits (IROL).

## Slide 3: Standard TOP-002 Transmission Operations Planning
Purpose: Current operations plans and procedures are essential to being prepared for reliable operations, including response for unplanned events.
  Each Balancing Authority and Transmission Operator shall plan to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements.

## Slide 4: Standard TOP-004 Operations
Purpose: To ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies.
  R2. Each Transmission Operator shall operate so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency.

## Slide 5: Contingency Analysis
RTCA studies the N-1 and specified multiple Contingencies.
  Studies affirmatively indicate Outage of the N-1 or DCKT poses a significant risk of uncontrolled outages because it would result in equipment overloads, which cannot be eliminated through execution of specific, predefined operating procedures (i.e. RAPs)

## Slide 6: SCED Overview – Applicable Contingencies
ERCOT models all single transmission line, autotransformer, and generation unit contingencies
  This is performed using an automatic contingency generator application developed by the Network Modeling Department and has been discussed with the Network Data Support Working Group (NDSWG)
  Certain additional contingencies are defined manually in the CIM where the automatic contingency generator cannot be used
    Double-Circuits
      Modeled based on information received by Transmission Owners (discussed in previous NDSWG meetings)
    Multi-unit contingencies such as whole combined-cycle trains
    Additional multi-unit contingencies are modeled pursuant to ERCOT and NERC requirements (e.g. double STP or Comanche Peak)

## Slide 7: Contingencies used in Operations
ERCOT uses NMMS to generate the N-1 contingency list.
Additionally ERCOT uses NMMS to check existing double-circuit contingencies within NMMS. These are maintained. Under the posted OPERATIONS SUPPORT PROCEDURE-”DEFINITIONS AND MAINTENANCE OF CONTINGENCIES” http://planning.ercot.com/content/22547

## Slide 8: Use of the results from RTCA in SCED
Generic
constraints
Contingency
Analysis
RTCA
Stability interface
constraints
Active constraints
& shift factors
Transmission Constraint Management
Transmission
Constraint
Management
TCM
Contingency
constraints
& shift factors
Voltage Stability Analysis
Transient Stability Analysis
MMS
MIS
Constraint
information
Remedial Action
Plans
Dynamic
Remedial
Action Plan
DRAP
RAP, SPS
Notes: Real Time Contingency Analysis (RTCA) shall simulate contingencies for the real-time network and identify all resulting security violations. The MW and KV violations and their associated limits, along with the constraints, shall be made available to the Transmission Constraint Management (TCM) process, where the Transmission Operator shall have the ability to deactivate, activate, manually enter, edit, and override the limits of those constraints.

## Slide 9: Mitigation plans
Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions.
  Activate constraint if shift factors exist for ≥ 2%

## Slide 10: Mitigation Plan examples applicable to SCED irresolvable congestion
Ackerly Lyntegar – Sparenburg example

## Slide 11: Ackerly Lyntegar – Sparenburg Overload: Pre Contingency
Contingency
Constraint
TOAP
Contingency: Willow Valley to Lamesa Outage
Constraint: Ackerly Lyntegar – Sparenburg
Constraint Flow: 19.35 MVA

## Slide 12: Ackerly Lyntegar – Sparenburg Overload : Post Contingency
Contingency
Constraint
TOAP
Contingency: Willow Valley to Lamesa Outage
Constraint: Ackerly Lyntegar – Sparenburg
Constraint Flow: 35.67 MVA

## Slide 13: Ackerly Lyntegar – Sparenburg Overload : Post TOAP
Contingency
Constraint
TOAP
Contingency: Willow Valley to Lamesa Outage
Constraint: Ackerly Lyntegar – Sparenburg
Constraint Flow: 32.62 MVA

## Slide 14: Odessa North 138/69 kV Auto Overload : Pre Contingency
Contingency
Constraint
MP
Contingency: Holt Switch – Moss Switch Outage
Constraint: Odessa North 138/69 kV Auto
Constraint Flow: 51.56 MVA

## Slide 15: Odessa North 138/69 kV Auto Overload : Post Contingency
Contingency
Constraint
MP
Contingency: Holt Switch – Moss Switch Outage
Constraint: Odessa North 138/69 kV Auto
Constraint Flow: 68.48 MVA

## Slide 16: Odessa North 138/69 kV Auto Overload : Post MP
Contingency
Constraint
MP
Contingency: Holt Switch – Moss Switch Outage
Constraint: Odessa North 138/69 kV Auto
Constraint Flow: 24.97 MVA