## Slide 1: ROS Workshop on PGRR 0011
Comparison of NERC Standards to PGRR 0011
Congestion Reporting and Monitoring

## Slide 2: Congestion Reporting and Monitoring

## Slide 3: NERC vs. ERCOT Planning Criteria
NERC TPL Standards
Minimum criteria
ERCOT Planning Guide
Higher standard for ERCOT System
TSP Planning Criteria
Higher standard for individual TSP system

## Slide 4: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Combined Cycle Train contingency | Contingency is worst single unit outage; All facilities within applicable ratings; stable operation | Contingency is entire train regardless if units can operate separately; All facilities within applicable ratings; stable operation | Not specified | Not specified
Loss of generation unit, system adjustment, then next contingency | All facilities within applicable ratings; stable operation; load shed allowed | All facilities within applicable ratings; stable operation; No load shed allowed | All facilities within applicable ratings; stable operation; load shed allowed | All facilities within applicable ratings; stable operation; load shed allowed

## Slide 5: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Loss of autoxfmr, system adjustment, then next contingency | All facilities within applicable ratings; stable operation; load shed allowed | All facilities within applicable ratings; stable operation; No load shed allowed; | All facilities within applicable ratings; stable operation; load shed allowed | All facilities within applicable ratings; stable operation; load shed allowed; If lead time > 1 year then no load shed single contingency, load shed for some <300 kV SLG

## Slide 6: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Simultaneously secure feasible dispatch | Not specified | Must be done | Not specified | Not specified
Generic constraint limits from real-time | Per NERC criteria | Must be modeled in Planning | Planning Horizons SOLs should be modeld (FAC-010-2) | Planning Horizons SOLs should be modeld (FAC-010-2)

## Slide 7: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Load level variation | Reasonable variations | Reasonable variations may include 90th percentile load and non-weather driven forecast senstivities | Cover critical system conditions as deemed appropriate by responsible entity; Selected demand levels over the range of forecast system Demands | System peak and System Off Peak; Sensitivity may include variation to load forecast
Generation variation | Reasonable variations | Reasonable variations may include 90th percentile forced outages for a wide area | Not specified | Sensitivity may include generation retirements or other dispatch scenarios

## Slide 8: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Complete WGR or solar unavailability in a local or wide area | Reasonable variations | Reasonable variations including this specific criterion | Not specified | Sensitivity may include other dispatch scenarios
Dynamic line ratings | Not specified | May be included | Not specified | Not specified
Maintenance outages | Reasonable variations | Reasonable variations [with more specificity] | Include planned outages | Known outages of at least 6 months,
Ancillary services considerations | Not specified | Provisions must be made for RRS, Regulation Up, NSRS | Not specified | Not specified

## Slide 9: NERC vs. ERCOT Planning Criteria
Criterion | Current ERCOT PG | PGRR 0011 | TPL-00x-1 | TPL-001-2*
Generation Resource potential to solve problem | Not specified | ERCOT to study if project > $100M | Not specified | Not specified

## Slide 10: Congestion Reporting and Monitoring
Each month ERCOT calculates the congestion cost on all SCED congestion by multiplying the shadow price by the congested element rating and summing for the month
The top ten congested elements for each month and YTD are reported in the monthly System Planning ROS report
  A basic root cause analysis is conducted to determine if the congestion was outage related
  An analysis is also performed to determine if there is an existing project in TPIT that “might” address the congestion
  If the congestion does not appear to be outage related and if there is not a related TPIT project System Planning will informally investigate the root cause to determine if there are system conditions present that are not being accounted for in the ERCOT model