## Slide 1: Probabilistic System Adequacy Analysis
Dan Woodfin
Director, System Planning
ROS Workshop on PGRR011
October 21, 2011

## Slide 2: Background
At the December 2008 NERC Planning Committee (PC) meeting, the PC approved the formation of the task force with these two main deliverables in the scope:
  To evaluate approaches and models for composite generation and transmission (G&T) reliability assessment.
  To provide a common set of probabilistic reliability indices and recommend probabilistic-based work products that could be used to supplement the NERC’s long term reliability assessments.
At its December 2010 meeting, the PC approved the recommendations of the task force, including the following requirement (edited):
  All Metric Reporting Areas (i.e. ERCOT) will conduct a probability analysis (pursuant to the Methodology and Metrics document approved by the PC) and report the metric results to the NERC Reliability Assessment Subcommittee (RAS). Results will be due to the RAS six months after the LTRA is finalized. The initial LTRA referenced for this analysis is expected to be completed in October 2012.

## Slide 3: Overview
Conceptually, the requirement is to do a forward-looking, multi-area, probabilistic analysis of the system
This analysis would be similar to the loss-of-load events analysis that ERCOT performs in order to calculate the reserve margin level necessary to maintain a 1 day in 10 years level of reliability, considering the impact of:
  Load forecast uncertainty
  Random forced outages of resources
But, with the additional consideration of having transmission system limitations modeled at an appropriate level of detail
  Optimally, this would include full topology; however, it may be necessary to simplify the system due to computational limits

## Slide 4: Inputs
Area 1
Area 2
~
~
Generator Modeling:
Each generator would be modeled with
  Seasonal Capacity
  Forced Outage Rates
  Wind et al requires special modeling
Load Modeling:
Each area would be modeled with a:
  Chronological Load Forecast
  Prob. Distrib. of Forecast Uncertainty
Transmission Modeling:
Each pair of contiguous areas would be modeled as having a transmission interface with a N-1 Transfer /Interface Capacity, at least
Areas should be defined where transmission import limits into the area (or generation deficiencies within the area) could result due to combination of high loads and forced generation outages within the area
Area may be a single bus or an aggregated area; more aggregation requires more analysis to get appropriate transmission limits

## Slide 5: Conceptual ERCOT Representation
West Texas
North TX W
North TX E
DFW 138 W
Hill Co
Cen Tx
Houston
SA
So Tx
Lar
DFW 138 E
LRGV
Far West
This is only intended to illustrate the concept and allow for discussion; there is no analytics behind this representation
Number of areas will be a tradeoff between decision requirements and computational practicality/resources

## Slide 6: What does this have to do with PGRR-011???
Proposed PGRR-011 requires deterministic consideration of lower probability events (90th percentile loads, 90th percentile forced outages, etc.)
  Perception is that cost of mitigating the impacts of these events may be high
  Question is whether the transmission expenditure to mitigate these impacts is warranted or not
Use of probabilistic analysis would allow assessment of magnitude of the impact of an event, weighted by the likelihood of occurrence of the event
  Loss of load metric for the system may be exceeded, due to transmission limits into an area, indicating need to additional transmission into area or additional resources within area

## Slide 7: Complexity
Most of the complexity in this analysis is around the transmission modeling
  Appropriate selection of the areas
  Appropriate determination of the inter-area transfer limits
  Requirements to recalculate transfer limits for proposed transmission additions
Simulation run times may also be an issue
While the traditional 1 day in 10 years LOLEv metric is applied on a system-wide basis; an additional metric(s) may need to be determined to appropriately consider the reliability impacts on smaller areas

## Slide 8: Status
ERCOT has issued an RFP to procure vendor to develop databases and perform initial study to meet NERC requirement
  NERC requirement is for static assessment, not analysis of options
Ideally, ERCOT will license model used by vendor and use/update databases to perform studies in-house on an on-going basis
Resources are not in the budget for this activity

## Slide 9
Questions?