| PGRR Number | 013 | PGRR Title | New Section 6.3, Process for Developing Short Circuit Cases (Portion of SPWG Procedures) |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | October 28, 2011 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Planning Guide Sections Requiring Revision |  | 2.2, Acronyms 6.3, Process for Developing Short Circuit Cases (new) |  |  |
| Revision Description |  | This Planning Guide Revision Request (PGRR) proposes a new Section 6.3 to incorporate Section 4, Procedure for the Short Circuit Database, of the System Protection Working Group (SPWG) Procedures into the Planning Guide. This PGRR takes into account feedback received at the 6/15/11 Planning Working Group (PLWG) meeting. |  |  |
| Reason for Revision |  | This PGRR incorporates the process for the development of the short circuit cases used for planning purposes into the Planning Guide. |  |  |
| Procedural History |  | - On 9/30/11, PGRR013 was posted. - On 10/28/11, the Planning Working Group (PLWG) considered PGRR013. |  |  |
| PLWG Decision |  | On 10/28/11, the PLWG was in consensus to recommend approval of PGRR013 as revised by PLWG. |  |  |
| Summary of PLWG Discussion |  | On 10/28/11, the triggers for modeling new Resources were discussed and clarified. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | - Improves transparency and provides change mechanism for the planning processes. |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
|  | 5 |  |

| Sponsor |  |
| --- | --- |
| Name | Kris Koellner on behalf of the SPWG |
| E-mail Address | kristian.koellner@lcra.org |
| Company | LCRA |
| Phone Number | (512) 369-4573 |
| Cell Number |  |
| Market Segment | Cooperative |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Comments

Although the normal process is to introduce new language as redline, the PLWG agreed that since the language currently exists in the SPWG Procedures, only proposed changes will be shown as redline.

Proposed Guide Language Revision

2.2 Acronyms

FY		Future Year

CY		Current Year

6.3		Process for Developing Short Circuit Cases

This Section describes the process for the development of the short circuit cases used for planning purposes.  Operating Guide Section 6, Disturbance Monitoring and System Protection, describes other non-planning aspects relating to system protection and disturbance monitoring requirements.

(a)	ERCOT shall collect the short circuit data sets or data updates developed by each Transmission Service Provider (TSP) and shall compile and maintain the short circuit cases.

(b)	During the first quarter of each calendar year, ERCOT shall compile and distribute the Current Year (CY) short circuit case to the System Protection Working Group (SPWG).

(c)	During the second quarter of each calendar year, ERCOT shall compile and distribute the Future Year (FY) short circuit cases for years two through five to the SPWG.

(d)	The transmission and generation systems of each Facility owner in ERCOT shall be represented completely including positive and zero sequence data.  Generation Resource data shall be provided by the Resource Entity.

(e)	New Generation Resources will be included in the short circuit cases once ERCOT receives either:

(i)	A signed Standard Generation Interconnection Agreement (SGIA) or a public, financially-binding agreement between the generator and the TSP under which the generation interconnection Facilities would be constructed; or

(ii)	A commitment letter from a Municipally Owned Utility (MOU) or an Electric Cooperative (EC) building a Generation Resource.

(f)	Each common bus within both the short circuit case and the corresponding load flow case shall have a matching bus name and matching bus number.  Each additional bus added to the short circuit case as necessary to perform short circuit studies shall be assigned a name and bus number that does not conflict with pre-existing names and bus numbers used in the current set of load flow cases.

(g)	The positive sequence impedance of Transmission Elements used in both the load flow and short circuit cases shall be the same.

(h)	Zero sequence data shall include mutual impedance of multi-circuit transmission lines and of adjacent circuits within the same right-of-way, unless the TSP considers such impedance to be insignificant for studies made from this data.