ERCOT Operations Report

Oct 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 10/13/2011 0:44 | 59.804 | 76 | Unit trip with 602 MW online. |
| 10/13/2011 10:53 | 59.800 | 136 | Unit trip with 861 MW online. |
| 10/14/2011 8:19 | 59.863 | 40 | Unit trip with 613 MW online. |
| 10/15/2011 10:40 | 59.882 | 12 | Unit trip with 361 MW online. |
| 10/19/2011 8:50 | 59.831 | 54 | Unit trip with 704 MW online. |
| 10/24/2011 5:57 | 60.123 | 132 | Gen Deviation +1200 MW in 4 mins. Out of DRS. |
| 10/31/2011 5:58 | 60.102 | 8 | Gen Deviation +1000 MW in 4 mins. Out of DRS. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

None

RUC Commitments

| Weather Zone | Unit Days |
| --- | --- |
| COAST | 9 |
| EAST | 2 |
| FAR WEST | 1 |
| NORTH CENTRAL | 41 |
| SOUTH | 2 |
| SOUTH CENTRAL | 9 |
| Grand Total | 64 |

SCED Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Paint Creek - Aspermont 138 kV | Aspermont 138/69 kV XFMR1 | 21 |
| Basecase | Golden Switch - Brand (ONCOR) 138 kV | 11 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 9 |
| DCKT Austrop - Garfield & Zorn 345 kV | Austrop 345/138kV AT2 | 7 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 7 |
| DCKT Greens Bayou - Gable & Hardy - Crocket 138 kV | Garrott - Midtown 138 kV | 6 |
| Gail Sub - Key Sub 138 kV | Sparenburg - Lamesa 69 kV | 5 |
| Sun Switch - Golden Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 5 |
| STP - Elm Creek 345kV | Blessing - Lolita 138kV | 4 |
| STP - Blessing 345 kV | Columbus - Stafford 69 kV | 4 |
| DCKT WA Parish - Obrien 345 kV | Garrott - Midtown 138kV | 4 |
| DCKT STP - Hillje & Elmcreek 345 kV | Blessing - Lolita 138kV | 3 |
| Sonora - Live Oak AEP 138 kV | Eldorado - Live Oak AEP 69 kV | 3 |
| Oklaunion - Abilene Mulberry Creek 345 kV | Fisher Road Switch - Wichita Falls 138 kV | 3 |
| DCKT Watermill Switch - Limestone 345 kV | Jewett - Rattlesnake Rd Switch 345 kV | 2 |
| DCKT Watermill Switch - Limestone 345 kV | Limestone Plant - Jewett 345 kV | 2 |
| DCKT Graham - Long Creek 345 kV | Putnam 138/69 kV XFMR | 2 |
| Batesville - Pearsall 138 kV | Pearsall 138/69 kV XFMR | 2 |
| Channel Energy Center - Baytown Energy Center 138 kV | Baytown Energy Center 345/138 kV AT2 | 2 |
| DCKT Marion - Zorn & Clear Springs 345 kV | Seguin - Seguin West 138 kV | 2 |
| DCKT STP - Elmcreek & WA Parish 345 kV | STP - Hillje 345 kV | 2 |
| Fisher Road Switch - Wichita Falls 138 kV | Fisher Road Switch - Wind Creek 138 kV | 2 |
| Brownwood Switch - Zephyr BEPC138 kV | Downing - Rising Star 69 kV | 2 |
| DCKT STP - DOW 345 kV | STP - Hillje 345 kV | 2 |
| DCKT Singleton Tomball & Roans Prairie 345 kV | Singleton - Zenith 345 kV | 2 |
| Caney Creek - Dyann 138 kV | Lane City - Blessing 138 kV | 2 |
| Basecase | Ennis Creek Switch XFMR1 69/138 KV | 1 |
| Basecase | Sonora - Cauthorn 138 kV | 1 |
| DCKT Watermill Switch - Limestone 345 kV | Jewett - Big Brown SES 345 kV | 1 |
| DCKT Graham - Long Creek 345 kV | Fisher Road Switch - Wichita Falls 138 kV | 1 |
| North Edinburg - Rio Hondo 345 kV | Aderhold Sub - Elsa 138 kV | 1 |
| Lobo 345/138 kV XFMR #2 | Pearsall - Paloduro Sub 138 kV | 1 |
| DCKT Graham - Parker Switch 345 kV | Barton Switch - Oran Sub 138 kV | 1 |
| Meadow - Oasis 345 kV | Garrott - Midtown 138kV | 1 |
| Dyann - South Lane City 138 kV | Columbus - Stafford 69 kV | 1 |
| DCKT Odessa High Voltage - Morgan Creek SES &Quail Switch 345 kV | Midland East - Windwood 138 kV | 1 |
| Morgan Creek SES 345/138 kV Auto XFMR #2 | Morgan Creek SES 345/138 XFMR 2H | 1 |
| DCKT Greens Bayou - King 345 kV | Green Bayou 345/138 kV AXFMR2 | 1 |
| Tenaska TMPP - Concord 138 kV | Tenaska TMPP - Keene BEPC 138 kV | 1 |
| DCKT STP - Hillje & Whitepoint 345 kV | Franklins Camp Sub - Sargent Sub 69 kV | 1 |
| Sandow 5 - Sandow Switch 138 kV | Sandow SES - Sandow Switch 138 kV | 1 |
| San Angelo Red Creek - Comanche Switch 345 kV | Leon Switch - Flat Creek 138 kV | 1 |
| San Angelo Red Creek Switch - Twinbute 345 kV | San Angelo Red Creek 345/138 kV XFMR2 | 1 |
| Morgan Creek SES - Sun Switch 138Kv/6474 | Golden Switch - Brand (ONCOR) 138 kV | 1 |
| West Conoco - Asherton 138 kV | West Batesville - Uvalde 138 kV | 1 |
| Spur - Aspermont 138 kV | Golden Switch - Brand (ONCOR) 138 kV | 1 |
| Pawnee - Calaveras 345 kV | Blessing - Lolita 138kV | 1 |
| Bluff Creek Switch - Exxon Sharon Ridge 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| DCKT San Miguel - Elmcreek & Marion 345 kV | Marion - Skyline 345 kV | 1 |
| Oran Sub - Barton Switch 138 kV | Ivan Sub - Breckenridge 69 kV | 1 |
| DCKT Elmcreek - Hill Country & Skyline 345 kV | Marion - Skyline 345 kV | 1 |
| Zorn - Marion 345 kV | Clear Springs - Marion 345 kV | 1 |
| Lobo - San Miguel 345 kV | San Diego - Freer 69 kV | 1 |
| DCKT Garfield - Hicross & Onion - Pilot 138 kV | Austrop 345/138kV AT2 | 1 |
| DCKT Jewett - Singleton 345 kV | Tonkawa Switch - Jack Creek 345 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 20 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 10/03/2011 | Transmission and Security Desk V1 Rev11 | 562 |
| 10/03/2011 | Shift Supervisor Desk V1 Rev8 | 561 |
| 10/03/2011 | Resource Desk V1 Rev10 | 560 |
| 10/03/2011 | Real Time Desk V1 Rev11 | 558 |
| 10/03/2011 | DC Tie Desk V1 Rev9 | 557 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

09/03 17:00 49,452 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | 3.46 |
| March | 3.29 | 3.24 | 2.24 | 2.02 |
| April | 2.45 | 2.66 | 2.47 | 3.55 |
| May | 3.01 | 2.90 | 2.63 | 3.27 |
| June | 2.81 | 2.89 | 2.84 | 2.28 |
| July | 2.55 | 2.83 | 2.39 | 1.63 |
| August | 3.66 | 3.07 | 2.29 | 2.28 |
| September | 4.99 | 3.68 | 3.14 | 2.70 |
| October | 2.79 | 2.92 | 2.37 | 3.51 |
| November | 2.60 | 1.93 | 3.46 | NA |
| December | 4.54 | 3.70 | 2.60 | NA |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.76 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 10/1/2011 | 01:17 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 15:00 – 21:00 |
| 10/1/2011 | 07:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 17:00 – 19:00 |
| 10/1/2011 | 10:45 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/2/2011 | 16:25 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/3/2011 | 09:42 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00-19:00 |
| 10/4/2011 | 01:34 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 - 20:00 |
| 10/5/2011 | 02:45 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 – 18:00 |
| 10/6/2011 | 03:05 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 – 21:00 |
| 10/6/2011 | 20:15 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/7/2011 | 02:35 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 16:00 – 19:00 |
| 10/8/2011 | 08:10 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 13:00 – 18:00 |
| 10/8/2011 | 08:42 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/8/2011 | 09:43 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/12/2011 | 15:36 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/13/2011 | 02:20 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 14:00 – 21:00 |
| 10/13/2011 | 06:20 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/13/2011 | 14:46 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/15/2011 | 15:00 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/16/2011 | 15:03 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/21/2011 | 16:30 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/26/2011 | 10:22 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 14:00 – 20:00 |
| 10/26/2011 | 14:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/27/2011 | 23:23 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 10/30/2011 | 19:21 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |

Transmission Watch

10/09 12:30	ERCOT issued a Transmission Watch in Eagle Pass area due to forced outages.

Emergency Notice

None

Texas RE Event Analysis

None