| NPRR Number | 315 | NPRR Title | Revision of Responsive Reserve Measure to Net Dependable Capability |
| --- | --- | --- | --- |
| Date |  | November 1, 2011 |  |
| Submitter’s Information |  |  |  |
| Name |  | Clayton Greer |  |
| E-mail Address |  | Clayton.greer@morganstanley.com |  |
| Company |  | Morgan Stanley |  |
| Phone Number |  | 512-497-2986 |  |
| Cell Number |  | 512-639-3993 |  |
| Market Segment |  | Independent Power Marketers |  |

Comments

At PDCWG, discussion led to a possible alternative solution to this NPRR.  That solution was to modify the COP of a unit to include ancillary services not actually carried by the unit.  Specifically we discussed assigning capacity to a dummy ancillary service in an amount that would cause the resulting HASL to reflect the desired operating limit.  This would allow the QSE to leave the HSL at it’s original level and maintain the 20% limit on Responsive Reserve provision based on the HSL.

To ensure this would not cause other issues with the systems or operations, it was requested that a test be performed on this solution.  Morgan Stanley opted to utilize Non-Spin as the “dummy” ancillary service and successfully ran a test showing 10MWs of NSRS on the unit which resulted in a corresponding 10MW reduction in the unit’s HASL.  Non-spin was selected as it has the closest operating characteristics to the corresponding capacity (capacity that is reserved unless needed under extreme conditions).

Given that the test was successful, it appears this is a better alternative than the original language of the NPRR.  However, other questions should be resolved as a part of this solution:

- Is the addition of a “dummy” ancillary service simple and relatively costless to create?

- If the answer to (1) is no, is on line NSRS an acceptable alternative?

- If so, are there any Protocol, Guide or Procedure documents that need revision?

- Does ERCOT need any additional notification that a QSE is doing this?

- Does the effort to inject on-line NSRS capacity into the active SCED stack undo this fix?

If we can resolve the use of this alternative method, I would be happy to withdraw or modify this NPRR to incorporate the needed changes.

Revised Proposed Protocol Language