## Slide 1: Potential Planning & Operations Enhancements Luminant Energy
November 10, 2011
Notes: 11/7/2011
1

## Slide 2
2
Executive Summary
October 21, 2011 Special ROS Meeting
  We learned that ERCOT has 30 minutes to develop a Mitigation Plan (MP) for SCED Irresolvable events
    If they can do so, then there is no reliability issue in Operations.
    If they do not, then a transmission watch is issued (and very few were ever issued).
  Most of these MPs involve post-contingency load shed plan of some sort.
Key Questions to Answer
  Are we all comfortable with a heavy reliance on MPs involving load shed?
  Is that how the Board wants us to plan to operate the system?
Purpose of this Presentation
  Illustrate operational exposure still being missed by 5-Year Plan process
  Suggestions to streamline RPG process for 5-Year Plan reliability projects
  Request that ROS pursue LCRA’s suggestion to form an ah-hoc task force to take a closer look at these issues.
Notes: 11/7/2011
2

## Slide 3: Operational Exposure During August 2011 EEAs Review of Sample Post Contingency Loading During August 2011 EEA Events
3
Refer to slide 9 & 10 in the Appendix for more August 2011 EEA related post-contingency overloads

## Slide 4: Is the 5-Yr Plan Already Identifying These Issues? Examining data from 2PM to 8PM during July – August 2011 to minimize impact of transmission outages
4
One (1) of the 14 SCED non EEA “insecure” constraints1 were identified by the 5-Year Plan. Half have no TPIT project identified.
1) Insecure as described in Protocol Section 6.5.7.1.10 for 30 or more consecutive minutes
Note: non EEA related overloads in SCED
Congestion
Rent

## Slide 5: How Long Do These Overloads Typically Last? View of Post Contingency Loading of NW Carrollton – Lake Point 138 kV Line on select SCED Irresolvable Days
5
Post contingency overload duration 2.5X longer than SCED Irresolvable

## Slide 6: Are There Process Improvements That Can Help?
6
Of the 26 transmission upgrades recommended by the 5-Year Plan for summer 2011, few were implemented due to process barriers

## Slide 7: Are There Some Process Improvements That Can Help?
Timely 5-Year Plan – Establish an earlier, consistent publishing date for the 5-year plan.
  The 2010 5-Year Plan was published in March 2011.
  17 of 26 projects needed by summer 2011 had been newly identified in the 2010 Plan.
Optimize RPG Review Process – Streamline RPG approval process
  RPG review was required for many of the aforementioned projects (6-9 month delay)
  Exempt all 5-Year Plan ‘reliability’ endorsed projects costing less than $50 million
  Grant ‘urgent’ RPG review of all remaining projects with a need date of less than 36 months.
Facilitate RAP Development – Clarify assignment of responsibility for RAP development
  No clear linkage of RAP recommendation in 5-Year Plan to implementation
These suggested improvements can be reviewed further in the ad-hoc ROS task force.

## Slide 8: Appendix
Notes: 11/7/2011
8

## Slide 9: Operational Exposure During August 2011 EEAs Review of Sample Post Contingency Loading During August 2011 EEA Events
9

## Slide 10
10
Four (4) of the top 20 EEA post-contingency overloads were identified
Note: this is the top 20 (in max loading) out of 72 EEA related overloads
Is the 5-Yr Plan Already Identifying These Issues? Examining data from EEA time periods during of August 2011 to minimize impact of transmission outages

## Slide 11: How Long Do These Overloads Typically Last?
11
During a sample 2 week period in July1, the NSA2 > 100% for ~32 hours
1) By late July, Luminant proposed a RAP that ERCOT implemented on August 2, 2011. 2) NSA is Network Security Analyzer

## Slide 12
12
Co-Benefits Of Increased Operational Efficiency
During the first 10 months after Nodal Go-Live, 32% of all congestion cost occurred due to SCED irresolvable episodes lasting 30+ minutes
$588 Million total congestion rent
$191 Million SCED Irresolvable congestion rent
Notes: 11/7/2011
12