Guidelines for Applying

IEEE Transmission Protective Relay System Performance Measuring Methodology (k-Factor)

| # | Operation Example | # Misoperation/ #k-factor | Reason |
| --- | --- | --- | --- |
| 1 | 138 kV Bus Differential false trips clearing bus and 5 transmission line terminals |  | Are we counting terminals that false trip or relay/relay systems? Section 3.4 of the guide states “each terminal that misoperates should be counted as a misoperation”. |
| 2 | Multiple relays on line terminal (e.g. primary and backup) over-reach and trip for an out-of-zone fault due to incorrect Zone 1 reach setting |  | If we are counting relays or relay systems, would this then be counted as 1 misoperation or 2 misoperations |
| 3 | Breaker trip coil(s) fail resulting breaker failure operation. |  | Trip coil is now considered part of protection system, so should this be considered a misoperation? |
| 4 | Relay misoperates for an out-of-zone fault. System Operator manually closes breaker via SCADA a couple of minutes later and relay misoperates for same fault or condition. |  | Should this count as a “subsequent closure into a fault” and count as 1 misoperation or be counted as two separate misoperations. |
| 5 | Carrier On-Off Block Signal has been disabled. A fault occurs resulting in a trip of one of the terminals because of no block signal received in a Directional Comparison Blocking scheme. |  |  |
| 6 | Protection is set knowingly with a miscoordination that will occur in certain circumstances with the terminal tripping of an out-of-zone fault. The contingency has been documented and studied to cause no known reliability issues. |  |  |
| 7 | On a tie-line, relaying at Utility A detects a fault in the forward direction but does not receive a block from Utility B’s remote terminal. |  | Who should record as misoperation? |