| NOGRR Number | 074 | NOGRR Title | Clarified Responsible Entities for Reporting Sabotage Information to NERC |
| --- | --- | --- | --- |

| Date | November 23, 2011 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Christine Hasha |
| E-mail Address | chasha@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3909 |
| Cell Number | 512-971-6906 |
| Market Segment | N/A |

Comments

ERCOT submits these comments to Section 3.8, Requirements for Reporting Sabotage Information to help clarify responsibilities for reporting sabotage events.

Revised Proposed Guide Language

3.7.3	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15-minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Elements to within Normal Ratings as soon as practicable, based on Good Utility Practice.

- 3.8	Requirements for Reporting Sabotage Information

(1)   	 ERCOT Entities shall notify their designated Transmission Operator (TO) or Qualified Scheduling Entity (QSE) when experiencing disturbances or unusual occurrences suspected or determined to be caused by sabotage.  Disturbances and unusual occurrences related to bulk electric system Facilities within the ERCOT Region are the only Facilities subject to reporting.  ERCOT Entities shall have procedures for the recognition of sabotage events on its Facilities and multi-site sabotage.

(2)    	TOs or QSEs shall inform ERCOT of disturbances or unusual occurrences suspected or determined to be caused by sabotage.  TOs or QSEs may notify ERCOT by telephone or by email at shiftsupervisors@ercot.com.

(3)   	 TOs and QSEs may inform other ERCOT Entities of the event(s), if, in the opinion of the TO or QSE, the situation impacts other Entities.

(4)    	ERCOT may inform TOs and QSEs of the event(s), if, in the opinion of ERCOT, the situation impacts ERCOT System reliability.

(5)    	ERCOT shall inform North American Electric Reliability Corporation (NERC) and governmental agencies of disturbances or unusual occurrences suspected or determined to be caused by sabotage in accordance with current laws and regulations.  This is in addition to the report submitted by the NERC registered Entity.