| NPRR Number | 394 | NPRR Title | Outage Reporting |
| --- | --- | --- | --- |
| Date |  | October 12, 2011 |  |
| Submitter’s Information |  |  |  |
| Name |  | Sherry Looney |  |
| E-mail Address |  | sherry.looney@luminant.com |  |
| Company |  | Luminant Energy |  |
| Phone Number |  | (214) 875-9278 |  |
| Cell Number |  | (469) 688-7607 |  |
| Market Segment |  | Investor-Owned Utility (IOU) |  |

Comments

Luminant Energy Company, LLC (Luminant) submits these comments to NPRR394, Outage Reporting to revise the requirement for reporting Generation Resource derates into the Outage Scheduler.  The revised Protocol language specifies the minimum MW level of derates for which reporting is required.  The original Protocol requirement was for 10% of High Sustainable Limit (HSL) for Resources less than 500 MW capacity and 2% of HSL for Resources greater than 500 MW capacity.  This revision changes that requirement to the maximum of 10 MW or 5% of HSL for all Generation Resources. Real Time capacity is reported through telemetry and Day Ahead and Balance of Day capacity are reported through the Current Operating Plan.  These are the critical measures used for capacity availability in ERCOT dispatch and unit commitment processes to ensure reliability.    This Protocol revision will simplify the Resource derate reporting requirement without compromising reliability.

Revised Proposed Protocol Language

- 2.1	Definitions

- Forced Derate

The portion of the Resource removed from service which exceeds the maximum of ten MW or 5% of its prior HSL for all Generation Resources.  For Qualified Scheduling Entities (QSEs) representing Wind-powered Generation Resources (WGRs), the loss of a portion of the capacity shall be due to the unavailability of a portion of the equipment and shall not include capacity changes due to changes in wind speed at the WGR facility.  For QSEs representing WGRs, the percentage calculation will be determined using the seasonal net maximum sustainable rating of the WGR.

- 3.1.4.8	Deratings

The Resource Entity or its designee must enter material deratings that are expected to last more than 48 hours in the ERCOT Outage Scheduler.  A derating is considered to be material when the Resource’s capability is reduced by the maximum of ten MW or 5% of its prior HSL for all Generation Resources.  For QSEs representing Wind-powered Generation Resources (WGRs), the loss of a portion of the capacity shall be due to the unavailability of a portion of the equipment and shall not include capacity changes due to changes in wind speed at the WGR facility.  For QSEs representing WGRs, the percentage calculation will be determined using the seasonal net maximum sustainable rating of the WGR.  ERCOT will consider the Resource’s capability as the lesser of the latest seasonal Net Dependable Capability test, or the resource registration process.