## Slide 1: Resource Adequacy Assessment December Update
Dan Woodfin
Director, System Planning
TAC
12/1/2011

## Slide 2: Context
Capacity, Demand and Reserves (CDR) Report typically released in December and May
Analysis of peak days this summer noted differences between May CDR inputs / assumptions and actual reserve availability during August 2011
  At the September Board meeting, ERCOT proposed several improvements to the CDR, as well as the creation of a new report – the Seasonal Assessment of Resource Adequacy (SARA) – to facilitate understanding of near-term risks
    SARA would be based on most-current available projections of inputs
    Inputs to SARA would be deterministic ranges; comparison would not be made to target reserve margin
  These concepts have continued to evolve over last two months, through discussions with the Generation Adequacy TF, the Regional Planning Group, and during the formulation of the reports

## Slide 3: Outline
Capacity, Demand and Reserves (CDR) Update
  Changes since May 2011 CDR
  Load Forecast
  CDR
  Interconnection Queue Project Status Update
Seasonal Assessment of Resource Adequacy (SARA) for Winter 2011/2012
  Sensitivities
  Winter SARA
Release Schedule for future SARAs and CDRs

## Slide 4: Changes that affect Reserve Margin since June 2011 CDR (for Summer 2012)
-1% reserve margin impact
-4% reserve margin impact
Jack County 2 (565MW) and Sherbino Mesa Wind 2 (150MW with ELCC of 13MW) moved from Planned to Installed)

## Slide 5: Load Forecast
Updated economic forecast from Moody’s
  Slower growth in near-term
Updated assessment of normal weather profile
Non-Farm Employment
Peak Demand
Non-Farm Employment
Peak Demand

## Slide 6: CDR Summary

## Slide 7: Generation Interconnection Queue Update
ERCOT requested each Transmission Service Provider (TSP) perform a comprehensive assessment/update of the current status of each of their assigned generation interconnection studies.
Several studies had been cancelled, and others had been “suspended” by agreement between the TSP and the generation developer, but could be reactivated and completed by similar agreement.
The table below shows the MW by fuel type of interconnection studies that were changed from “active” to either “cancelled” or “suspended” as a result of this survey:
Fuel Type | Cancelled Studies | Suspended Studies
 | (MW) | (MW)
Gas-AllOther |  | 
Gas-CombinedCycle | 1,939 | 2,890
Total Gas | 1,939 | 2,890
Nuclear |  | 2,700
Coal |  | 
Wind | 4,525 | 12,554
Solar | 236 | 353
Biomass |  | 50
Other | 700 | 
Grand Total | 7,400 | 18,547

## Slide 8: Reserve Margin, with Potential Resources from Queue
* Fuel Composition of Projects Undergoing Full Interconnection Studies - these projects may be cancelled or delayed beyond the indicated commercial dates shown
** Potential in-service dates for suspended projects shown as the later of 2013 or the date provided by the developer in their last update prior to suspension; may not reflect feasible in-service dates
Installed Capacity and Planned Units are included in the CDR (top of light blue bar)
Uncommitted Projects are not included in CDR
Uncommitted Projects

## Slide 9: Reserve Margin, with Potential Resources from Queue
* Fuel Composition of Projects Undergoing Full Interconnection Studies - these projects may be cancelled or delayed beyond the indicated commercial dates shown
** Potential in-service dates for suspended projects shown as the later of 2013 or the date provided by the developer in their last update prior to suspension; may not reflect feasible in-service dates
Installed Capacity and Planned Units are included in the CDR (top of light blue bar)
Uncommitted Projects are not included in CDR
Uncommitted Projects
Note: Reserve margin is amount by which resources exceed load. As load grows over time and exceeds the capacity of existing resources, the contribution of existing resources to the reserve margin will drop below zero

## Slide 10
Seasonal Assessment of Resource Adequacy (SARA) for Winter 2011/2012

## Slide 11: SARA Concept
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering resource adequacy for a near-term season
  Specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner – information that is not available for the long-term timeframe of the CDR.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur. Sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy.
  The variation in these parameters is either based on historic values of these parameters, adjusted by any known or expected change.

## Slide 12: SARA Calculation
Calculate available reserves based on available resources (excluding resources that are only used in EEA) and normal weather load forecast from CDR
Evaluate range of uses of reserves in a deterministic manner
  Uses of reserves:
    Higher peak demands due to above normal weather
    Forced generation outages
    Planned generation outages
    Atypical issues like drought
    Lower wind availability
Determine the extent by which reserves exceed the uses of reserves, in comparison to the 2300 MW level at which EEA would be declared

## Slide 13: Boundary Scenarios

## Slide 14: Future CDR and SARA Releases
CDR
  June release for Year+1 to Year+10 summer and winter (e.g. June 2012 release will not include 2012 summer)
  December release Year+1 to Year+10 summer
  This is same schedule as previous
SARA
  Preliminary release 3 ½ months prior to season and final release 1 ½ months prior to season
    February 15th – release Final Spring 2012 SARA and Preliminary Summer 2012 SARA
    April 15th – release Final Summer 2012 SARA
    May 15th – release Preliminary Fall SARA
    August 15th – release Final Fall SARA and Preliminary Winter SARA

## Slide 15
Questions?