## Base and Extreme
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2011-2012
Released December 1, 2011
Range of Likely Risks
|  | Installed Capacity, MW | 64363 | Based on current Seasonal Maximum Sustainable Limits reported through Registration process
|  | Planned Units (not wind) with Signed IA and Air Permit, MW | 30 | Based on in-service dates provided by developers of generation resources
|  | Capacity from Private Networks, MW | 4390 | Based on actual net PUN output during non-EEA periods of August 2011
|  | Switchable Units, MW | 3168 | Installed capacity of units that can switch to other Regions
|  | less Switchable Units Unavailable to ERCOT, MW | -317 | Based on survey response of Switchable Unit owners
|  | RMR Units to be under Contract, MW | 0
|  | Effective Load-Carrying Capability (ELCC) of Wind Generation, MW | 834.0727 | Based on 8.7% of installed capacity (Effective Load Carrying Capability) of wind per Planning Guide Section 8
|  | ELCC of Planned Wind Units with Signed IA, MW | 0 | Based on in-service dates provided by developers of generation resources
|  | 50% of Non-Synchronous Ties, MW | 553 | Based on 50% of installed capacity of ties, per Planning Guide Section 8
a | Total Resources, MW |  | 73021.0727
b | Winter Peak Demand, MW |  | 53562 | Updated 50% Probability forecast based on recent Moody's economic forecast and revised weather profile including 2011 impacts
c | Reserve Capacity (a -b), MW |  | 19459.0727
|  |  | Base Case |  | Extreme Conditions | Extreme/ Full Drought Impact * | * - Column added due to current drought risk
|  | Extreme Load Range | 0 |  | 6427 | 6427
|  | Typical Maintenance Outages | 5268 |  | 5268 | 5268
|  | 90th Percentile Maintenance Outages | 0 |  | 4244 | 4244
|  | Typical Forced Outages | 3759 |  | 3759 | 3759
|  | 90th Percentile Forced Outages |  |  | 2645 | 2645
|  | Forced Outages due to Drought (minimum) | 24 |  | 24
|  | Forced Outages due to Drought (maximum) | 0 |  |  | 11464
d | Total Uses of Reserve Capacity |  | 9051 |  | 22367 | 33807
e | Capacity Available for Operating Reserves (c-d), MW |  | 10408.0727 |  | -2907.9273 | -14347.9273
Less than 2300 MW indicates risk of EEA1

## Full Set of Sensitivities
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2011-2012
Released December 1, 2011
Analysis of All Sensitivities
|  |  | 64363 | Based on current Seasonal Maximum Sustainable Limits reported through Registration process
|  | Installed Capacity, MW | 30 | Based on in-service dates provided by developers of generation resources
|  | Planned Units (not wind) with Signed IA and Air Permit, MW | 4390 | Based on actual net PUN output during non-EEA periods of August 2011
|  | Capacity from Private Networks, MW | 3168 | Installed capacity of units that can switch to other Regions
|  | Switchable Units, MW | -317 | Based on survey response of Switchable Unit owners
|  | less Switchable Units Unavailable to ERCOT, MW | 0
|  | RMR Units to be under Contract, MW | 834.0727 | Based on 8.7% of installed capacity (Effective Load Carrying Capability) of wind per Planning Guide Section 8
|  | Effective Load-Carrying Capability (ELCC) of Wind Generation, MW | 0 | Based on in-service dates provided by developers of generation resources
|  | ELCC of Planned Wind Units with Signed IA, MW | 553 | Based on 50% of installed capacity of ties, per Planning Guide Section 8
|  | 50% of Non-Synchronous Ties, MW | 73021.0727
a | Total Resources, MW
b | Winter Peak Demand, MW |  | 53562 | Updated 50% Probability forecast based on recent Moody's economic forecast and revised weather profile including 2011 impacts
c | Reserve Capacity (a -b), MW |  | 19459.0727
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
|  |  | Expected Load, No Drought Impact |  |  | Extreme Load, No Drought Impact |  |  | Expected Load, Full Potential Drought Impact |  |  | Extreme Load, Full Potential Drought Impact
|  |  | Typical Forced and Planned Outages | High Forced Outages | High Forced and Planned Outages | Typical Forced and Planned Outages | High Forced Outages | High Forced and Planned Outages | Typical Forced and Planned Outages | High Forced Outages | High Forced and Planned Outages | Typical Forced and Planned Outages | High Forced Outages | High Forced and Planned Outages
|  |  | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727 | 19459.0727
|  | Extreme Load Range | 0 | 0 | 0 | 6427 | 6427 | 6427 | 0 | 0 | 0 | 6427 | 6427 | 6427
|  | Typical Maintenance Outages | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268 | 5268
|  | 90th Percentile Maintenance Outages | 3: 4244; 6: 4244; 9: 4244; 12: 4244
|  | Typical Forced Outages | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759 | 3759
|  | 90th Percentile Forced Outages |  | 2645 | 2645 |  | 2645 | 2645 |  | 2645 | 2645 |  | 2645 | 2645
|  | Forced Outages due to Drought (minimum) | 1: 24; 2: 24; 3: 24; 4: 24; 5: 24; 6: 24
|  | Forced Outages due to Drought (maximum) | 7: 11464; 8: 11464; 9: 11464; 10: 11464; 11: 11464; 12: 11464
d | Total Uses of Reserve Capacity, MW |  | 9051 | 11696 | 15940 | 15478 | 18123 | 22367 | 20491 | 23136 | 27380 | 26918 | 29563 | 33807
e | Capacity Available for Operating Reserves (c-d), MW |  | 10408.0727 | 7763.0727 | 3519.0727 | 3981.0727 | 1336.0727 | -2907.9273 | -1031.9273 | -3676.9273 | -7920.9273 | -7458.9273 | -10103.9273 | -14347.9273
Less than 2300 MW indicates risk of EEA1 | bar: 4
2300
2300
2300

## CDR Summary used as input
Winter Inputs
2012
Load Forecast:
| Total Summer Peak Demand, MW | 53562 | Updated 50% Probability forecast based on recent Moody's economic forecast and revised weather profile including 2011 impacts
| less Energy Efficiency Programs (per SB1125) | 119 | Projected based on SB1125 assuming that 50% of the energy efficiency target is included in the model
| less LAARs Serving as Responsive Reserve, MW | 1038 | Projected based on Planning Guide Section 8
| less Emergency Interruptible Load Service | 420 | Projected based on Planning Guide Section 8
| Firm Load Forecast, MW | 51985
Resources:
| Installed Capacity, MW | 64363 | Based on current Seasonal Maximum Sustainable Limits reported through Registration process
| Capacity from Private Networks, MW | 4390 | Based on actual net PUN output during non-EEA periods of August 2011
| ELCC* of Wind Generation, MW | 834.0727 | Based on 8.7% of installed capacity (Effective Load Carrying Capability) of wind per Planning Guide Section 8
| RMR Units to be under Contract, MW | 0
| Operational Generation, MW | 69587.0727
| Non-Synchronous Ties, MW | 553 | Based on 50% of installed capacity of ties, per Planning Guide Section 8
| Switchable Units, MW | 3168 | Installed capacity of units that can switch to other Regions
| Available Mothballed Generation , MW | 495.65 | Based on sum of Installed Capacity of each Mothballed Unit times Probability of Return to Service from survey response by owner of the Unit
| Planned Units (not wind) with IA and Air Permit, MW | 30 | Based on in-service dates provided by developers of generation resources
| ELCC* of Planned Wind Units with Signed IA, MW | 0 | Based on in-service dates provided by developers of generation resources
| Total Resources, MW | 73833.7227
| less Switchable Units Unavailable to ERCOT, MW | 317 | Based on survey response of Switchable Unit owners
| less future Unit Retirements, MW | 0
| Resources, MW | 73516.7227
Reserve Margin (Resources - Firm Load Forecast)/Firm Load Forecast |  | 41.42%
*Effective Load-Carrying Capability

## Inputs for Sensitivities
Scenario Inputs |  | Expected Load Adder | 0
|  | Extreme Load Adder | 6427 | Based on load forecast using actual extreme weather year (2011) temperatures
|  | Typical Maintenance Outages | 5268 | Based on average of historic planned outages for hour ending 7-10 of Dec,Jan,Feb weekdays
|  | 90th Percentile Maintenance Outages | 4244 | Based on historic planned outages for hour ending 7-10 of Dec,Jan,Feb weekdays
|  | Typical Forced Outages | 3759 | Based on average of historic forced and maint-level outages for hour ending 7-10 of Dec,Jan,Feb weekdays
|  | 90th Percentile Forced Outages | 2645 | Based on historic forced and maint-level outages for hour ending 7-10 of Dec,Jan,Feb weekdays
Low Wind
|  | Forced Outages due to Environmental Restrictions |  | Monticello 1&2 mothballing already included in Installed Capacity
|  | Forced Outages due to Drought (minimum) | 24 | Current unavailability
|  | Forced Outages due to Drought (maximum) | 11464 | MW of generation with water sources that are currently at historic lows
Total Uses of Reserves