| NPRR Number | 334 | NPRR Title | Incorporate Resource Limit for the amount of Regulation Service that may be provided from a Generation Resource during any Operating Hour |
| --- | --- | --- | --- |
| Date |  | August 11, 2011 |  |
| Submitter’s Information |  |  |  |
| Name |  | Sydney Niemeyer on behalf of the Performance Disturbance Compliance Working Group (PDCWG) |  |
| E-mail Address |  | Sydney.niemeyer@nrgenergy.com |  |
| Company |  | NRG Energy |  |
| Phone Number |  | 713-537-3715 |  |
| Cell Number |  | 832-655-0410 |  |
| Market Segment |  | Generator |  |

Comments

The PDCWG believes that the initial value of X% should be set at 30%.  This is based on the average Primary Frequency Response of the ERCOT System that since Dec 1, 2010 is approximately -490 MW/0.1 Hz.  The momentary loss of 30% of Regulation Service from a single Resource would impact ERCOT System frequency approximately +/-0.0613 Hz which is well within the frequency trigger limit of the BAAL field trial.  With SCED’s ability to recover Regulation Service every five minutes, the loss of Regulation Service will be minimized.  The 30% limit will require a minimum of four Resources to provide the service.

Revised Proposed Protocol Language Revision

- 3.16	Standards for Determining Ancillary Service Quantities

(1)	ERCOT shall comply with the requirements for determining Ancillary Service quantities as specified in these Protocols and the Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the minimum quantity requirements for each Ancillary Service needed for reliability, including the percentage of Load Resources excluding Controllable Load Resources, the percentage of Direct Current Tie (DC Tie), the percentage of Controllable load Resources allowed to provide Responsive Reserve (RRS) calculated on a monthly basis, and the limiting percentage of the total amount of each Ancillary Service needed for reliability that may be provided from any single Resource.

(3)	The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements and the monthly percentage of Load Resources, Controllable Load Resources, DC Ties allowed to provide RRS, and the limiting percentage of the total amount of each Ancillary Service needed for reliability that may be provided from any single Resource.

(4)	If ERCOT determines a need for additional Ancillary Service Resources under these Protocols or the Operating Guides, after an Ancillary Service Plan for a specified day has been posted, ERCOT shall inform the market by posting notice on the Market Information System (MIS) Secure Area, of ERCOT’s intent to procure additional Ancillary Service Resources under Section 6.4.8.2, Supplemental Ancillary Services Market.  ERCOT shall post the reliability reason for the increase in service requirements.

(5)	ERCOT shall post engineering studies on the MIS Secure Area representing specific Ancillary Service requirement on an annual basis.

(6)	The amount of Load Resources on high-set under-frequency relays providing RRS is limited to 50% of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation Service to be deployed.

(7)	The amount of RRS that a Qualified Scheduling Entity (QSE) can self-arrange using a Load Resource excluding Controllable Load Resources is limited to the lower of:

(a)	50% of its RRS Obligation; or

(b)	A reduced percentage of its RRS Obligation based on the limit established by ERCOT in paragraph (6) above.

- (8)	However, a QSE may bid more of the Load Resource above the percentage limit established by ERCOT for sale of RRS to other Market Participants.  The total amount of RRS using the Load Resource excluding Controllable Load Resources procured by ERCOT is also limited to the lesser of the 50% limit or the limit established by ERCOT in paragraph (6) above.

- 3.18	Resource Limits in Providing Ancillary Service

(1)	For both Generation Resources and Load Resources, the High Sustained Limit (HSL) must be greater than or equal to the Low Sustained Limit (LSL) and the sum of the Resource-specific designation of capacity to provide Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), and Non-Spinning Reserve (Non-Spin).

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

(3)	For RRS Service:

(a)	The amount of RRS provided from a Generation Resource must be less than or equal to 20% of thermal unit HSL for an Ancillary Service Offer and must be less than or equal to ten times the Emergency Ramp Rate;

(b)	Hydro-powered Resources operating in the synchronous condenser fast-response mode may provide RRS up to the Resource’s proved 20-second response (which may be 100% of the HSL);

(c)	For any hydro-powered Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 20% of the HSL; and

(d)	The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

(4) 	For Regulation Service:

(a)	The QSEs providing Regulation Service shall ensure that the amount of Reg-Up or Reg-Down provided from any single Generation Resource during any Operating Hour is less than or equal to X% of the Day-Ahead Ancillary Service Plan requirement for the corresponding Regulation Service for that Operating Hour.  The initial value of X% shall be 30%.  ERCOT shall determine the value of X% at least annually as part of its methodology for determining minimum quantity requirements for each Ancillary Service needed for reliability pursuant to paragraph (2) of Section 3.16, Standards for Determining Ancillary Service Quantities.

(b)	If ERCOT determines in the Adjustment Period that more Ancillary Services are needed as described in Section 6.4.8.1.1, ERCOT Increases to the Ancillary Services Plan, then the QSEs providing Regulation Service shall ensure that the amount of Reg-Up or Reg-Down provided from any single Generation Resource during any Operating Hour is less than or equal to X% of the revised Ancillary Service Plan requirement for that service for that Operating Hour.

[NPRR334: Replace paragraph (4) above with the following upon system implementation:] (4) For Regulation Service: (a) The amount of Reg-Up or Reg-Down awarded in the Day-Ahead Market (DAM) to any single Generation Resource for any Operating Hour must be less than or equal to X% of the Day-Ahead Ancillary Service Plan requirement for the respective Regulation Service for that Operating Hour. (b) If ERCOT determines in the Adjustment Period to open the Supplemental Ancillary Services Market (SASM) for undeliverable Regulation Service or Regulation Ancillary Service Failure to provide or ERCOT determines that more Ancillary Services are needed as described in Section 6.4.8.1.1, ERCOT Increases to the Ancillary Services Plan, then the amount of Regulation Service awarded in SASM to any single Generation Resource for any Operating Hour plus the amount of corresponding Regulation Service responsibility in the Current Operating Plan (COP) for the Generation Resource must be less than or equal to X% of the revised Ancillary Service Plan requirement for that service for that Operating Hour. (c) The QSEs providing Regulation Service shall ensure that the amount of Reg-Up or Reg-Down provided from any single Generation Resource during any Operating Hour is less than or equal to X% of the Day-Ahead Ancillary Service Plan requirement for the corresponding Regulation Service for that Operating Hour. If ERCOT increases the Ancillary Service Plan in the Adjustment Period, then the amount of Regulation Service Responsibility provided on any single Generation Resource should not exceed X% of the revised Ancillary Service Plan requirement for that service for that Operating Hour. (d) Initially and, at least annually thereafter, ERCOT shall establish the limiting value of X% described in paragraphs (4)(a), (4)(b), and (4)(c) above as part of its methodology for determining minimum quantity requirements for each Ancillary Service needed for reliability pursuant to paragraph (2) of Section 3.16, Standards for Determining Ancillary Service Quantities.