## Slide 1: December 2011 Generation Resource Energy and Regulation Deployment Performance
QMWG 1/6/2012

## Slide 2: Month-to-Month NON-IRR GREDP – Energy Deployments
Resources below 85% threshold
QSE Name | Resource Name | Fuel Type | Total Intervals Passed | Total Intervals Scored | Std Dev(GREDP MW) | GREDP Monthly Score
QSE1 | <RESOURCE NAME> | CC | 945 | 1,128 | 10.85 | 83.78
QSE2 | <RESOURCE NAME> | SCLE90 | 60 | 82 | 6.01 | 73.17
QSE3 | <RESOURCE NAME> | GSREH | 129 | 153 | 24.26 | 84.31
QSE4 | <RESOURCE NAME> | CC | 12 | 22 | 7.05 | 54.55
QSE4 | <RESOURCE NAME> | SCLE90 | 61 | 72 | 3.62 | 84.72
QSE4 | <RESOURCE NAME> | SCLE90 | 45 | 56 | 3.81 | 80.36
QSE4 | <RESOURCE NAME> | SCLE90 | 11 | 18 | 4.58 | 61.11
QSE5 | <RESOURCE NAME> | SCGT90 | 0 | 2 | 0.15 | 0.00
QSE5 | <RESOURCE NAME> | SCGT90 | 0 | 4 | 0.24 | 0.00
QSE5 | <RESOURCE NAME> | SCLE90 | 9 | 13 | 8.22 | 69.23
Chart: NON-IRR GREDP Summary
| July 2011 | August 2011 | September 2011 | October 2011 | November 2011 | December 2011
Passed | 325 | 335 | 340 | 296 | 254 | 275
Failed | 2 | 1 | 1 | 3 | 8 | 10
% Passed | 0.99388 | 0.99702 | 0.99707 | 0.98997 | 0.96947 | 0.96491

## Slide 3: Month-to-Month NON-IRR GREDP – Regulation Deployments
Resource below 85% threshold
QSE Name | Resource Name | Fuel Type | Total Intervals Passed | Total Intervals Scored | Std Dev(GREDP MW) | GREDP Monthly Score
QSE1 | <RESOURCE NAME> | CC | 26 | 34 | 24.82 | 76.47
Chart: NON-IRRs GREDP Summary - Providing Regulation
| July 2011 | August 2011 | September 2011 | October 2011 | November 2011 | December 2011
Passed | 140 | 146 | 163 | 128 | 93 | 105
Failed | 1 | 3 | 2 | 1 | 1 | 1

## Slide 4: Month-to-Month IRR GREDP
Resources below 95% threshold
 | Sep-11 | Oct-11 | Nov-11 | Dec-11
< 10 Intervals | 8 | 7 | 16 | 9
>=10<100 Intervals | 9 | 6 | 12 | 16
>=100<500 Intervals | 9 | 4 | 4 | 13
>=500 Intervals | 1 | 10 | 10 | 7
Weighted Averaged GREDP * | 87.2% | 91.1% | 92.2% | 88.9%
Average Deviation * | 9.8 MWs | 6.8 MWs | 8.0 MWs | 11.1 MWs
* Includes all WGRs (not just failures) |  |  |  | 
Chart: IRR GREDP Summary
| July 2011 | August 2011 | September 2011 | October 2011 | November 2011 | December 2011
Passed | 29 | 18 | 23 | 27 | 41 | 20
Failed | 23 | 38 | 27 | 27 | 42 | 35

## Slide 5: December IRR Failures
QSE Name | Resource Name | Total Intervals Passed | Total Intervals Scored | Std Dev (ATG-Exp MW) | GREDP Monthly Score
QSE1 | <RESOURCE NAME> | 839 | 902 | 7.52 | 93.02
QSE1 | <RESOURCE NAME> | 949 | 1,087 | 1.63 | 87.30
QSE2 | <RESOURCE NAME> | 324 | 360 | 19.83 | 90.00
QSE2 | <RESOURCE NAME> | 50 | 148 | 9.77 | 33.78
QSE3 | <RESOURCE NAME> | 439 | 478 | 12.08 | 91.84
QSE4 | <RESOURCE NAME> | 98 | 113 | 35.17 | 86.73
QSE4 | <RESOURCE NAME> | 12 | 16 | 7.73 | 75.00
QSE5 | <RESOURCE NAME> | 0 | 1 |  | 0.00
QSE5 | <RESOURCE NAME> | 0 | 1 |  | 0.00
QSE5 | <RESOURCE NAME> | 0 | 1 |  | 0.00
QSE5 | <RESOURCE NAME> | 1 | 2 | 0.88 | 50.00
QSE6 | <RESOURCE NAME> | 652 | 688 | 29.45 | 94.77
QSE6 | <RESOURCE NAME> | 18 | 19 | 9.93 | 94.74
QSE7 | <RESOURCE NAME> | 749 | 803 | 16.72 | 93.28
QSE7 | <RESOURCE NAME> | 1 | 2 | 8.83 | 50.00
QSE7 | <RESOURCE NAME> | 302 | 378 | 20.16 | 79.89
QSE7 | <RESOURCE NAME> | 539 | 635 | 32.22 | 84.88
QSE8 | <RESOURCE NAME> | 117 | 128 | 14.19 | 91.41
QSE9 | <RESOURCE NAME> | 1 | 3 | 18.64 | 33.33
QSE9 | <RESOURCE NAME> | 0 | 1 |  | 0.00
QSE9 | <RESOURCE NAME> | 1 | 8 | 6.11 | 12.50
QSE10 | <RESOURCE NAME> | 0 | 1 |  | 0.00
QSE11 | <RESOURCE NAME> | 532 | 582 | 1.40 | 91.41
QSE11 | <RESOURCE NAME> | 57 | 75 | 18.42 | 76.00
QSE11 | <RESOURCE NAME> | 450 | 610 | 6.68 | 73.77
QSE11 | <RESOURCE NAME> | 303 | 486 | 6.84 | 62.35
QSE12 | <RESOURCE NAME> | 446 | 474 | 2.42 | 94.09
QSE12 | <RESOURCE NAME> | 446 | 473 | 2.79 | 94.29
QSE12 | <RESOURCE NAME> | 417 | 467 | 1.45 | 89.29
QSE12 | <RESOURCE NAME> | 435 | 463 | 1.31 | 93.95
QSE13 | <RESOURCE NAME> | 153 | 222 | 25.96 | 68.92
QSE14 | <RESOURCE NAME> | 29 | 36 | 9.52 | 80.56
QSE14 | <RESOURCE NAME> | 33 | 44 | 9.25 | 75.00
QSE15 | <RESOURCE NAME> | 86 | 96 | 8.32 | 89.58
QSE16 | <RESOURCE NAME> | 295 | 337 | 6.95 | 87.54

## Slide 6: GREDP Scenario Analysis
* December performance of frequency excluded intervals for IRRs was 90% (1077 passed/1199 scored). November performance of frequency excluded intervals for IRRs was also 90% (2803 passed/3103 failed).
NON-IRRs (Dec-11) | >= 85% | < 85% | % Passing
5 MW | 178 | 107 | 62.46%
10 MW | 268 | 17 | 94.04%
15 MW | 282 | 3 | 98.95%
5 MW - 5% | 255 | 30 | 89.47%
8MW - 8% (Current) | 275 | 10 | 96.49%
Exclusions - No Freq Dev | 272 | 13 | 95.44%
IRRs (Dec-11) | >= 95% | < 95% | % Passing
0% - 3MW Band | 11 | 44 | 20.00%
5% - 3 MW Band | 15 | 40 | 27.27%
10% - 1MW Band when BP = 0 (Current) | 20 | 35 | 36.36%
10% - 3MW Band when BP = 0 | 20 | 35 | 36.36%
10% - 3MW Band at all times | 29 | 26 | 52.73%
Exclusions - No Freq Dev * | 20 | 35 | 36.36%

## Slide 7: Manual HDL/LDL Override Summary
QMWG 1/6/2012

## Slide 8: Daily Summary Graph
For this analysis, we captured unique HDL/LDL overrides
  An override is considered unique if that same Resource did not have an override within the last 10 minutes
There were 13 total unique overrides in December
  As compared to 17 in November and 18 in October
  All overrides were the result of transmission outages
Chart: Trend of Daily HDL/LDL Overrides

## Slide 9: Daily Summary Table
Date | Total Number of Overrides | Number of Resources with an Override | Number of Unique HDL/LDL Overrides
Dec 1, 2011 | 0 | 0 | 0
Dec 2, 2011 | 0 | 0 | 0
Dec 3, 2011 | 0 | 0 | 0
Dec 4, 2011 | 0 | 0 | 0
Dec 5, 2011 | 0 | 0 | 0
Dec 6, 2011 | 0 | 0 | 0
Dec 7, 2011 | 105 | 1 | 1
Dec 8, 2011 | 0 | 0 | 0
Dec 9, 2011 | 311 | 4 | 4
Dec 10, 2011 | 0 | 0 | 0
Dec 11, 2011 | 0 | 0 | 0
Dec 12, 2011 | 0 | 0 | 0
Dec 13, 2011 | 0 | 0 | 0
Dec 14, 2011 | 0 | 0 | 0
Dec 15, 2011 | 905 | 4 | 4
Dec 16, 2011 | 1,164 | 4 | 0
Dec 17, 2011 | 1,156 | 4 | 0
Dec 18, 2011 | 716 | 4 | 0
Dec 19, 2011 | 0 | 0 | 0
Dec 20, 2011 | 0 | 0 | 0
Dec 21, 2011 | 0 | 0 | 0
Dec 22, 2011 | 0 | 0 | 0
Dec 23, 2011 | 0 | 0 | 0
Dec 24, 2011 | 0 | 0 | 0
Dec 25, 2011 | 0 | 0 | 0
Dec 26, 2011 | 0 | 0 | 0
Dec 27, 2011 | 0 | 0 | 0
Dec 28, 2011 | 0 | 0 | 0
Dec 29, 2011 | 66 | 3 | 4
Dec 30, 2011 | 0 | 0 | 0
Dec 31, 2011 | 0 | 0 | 0