ERCOT Operations Report

Dec 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 12/14/2011 10:55 | 59.890 | 86 | Unit trip with 392 MW net. |
| 12/14/2011 12:46 | 59.819 | 137 | Unit trip with 560 MW net. |
| 12/14/2011 14:46 | 59.831 | 140 | Unit trip with 485 MW net. |
| 12/15/2011 13:16 | 59.792 | 132 | Unit trip with 600 MW net. |
| 12/18/2011 8:15 | 59.767 | 140 | Unit trip with 800 MW net. |
| 12/22/2011 5:15 | 59.800 | 114 | Unit trip with 760 MW net. |
| 12/26/2011 3:46 | 59.843 | 73 | Unit trip with 553 MW net. |
| 12/28/2011 9:49 | 59.796 | 128 | Unit trip with 719 MW net. |
| 12/30/2011 15:57 | 59.794 | 112 | Unit trip with 629 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 12/14/11 10:55:50 | 12/14/11 11:00:46 | 0:04:56 | 91.4 |  |
| 12/14/11 12:46:21 | 12/14/11 12:49:30 | 0:03:09 | 818.84 |  |
| 12/14/11 14:46:45 | 12/14/11 14:50:21 | 0:03:36 | 698.52 |  |
| 12/15/11 13:16:21 | 12/15/11 13:20:48 | 0:04:27 | 858.63 |  |
| 12/18/11 8:15:04 | 12/18/11 8:19:12 | 0:04:08 | 934.76 |  |
| 12/22/11 5:15:47 | 12/22/11 5:19:10 | 0:03:23 | 688.05 |  |
| 12/26/11 3:46:30 | 12/27/11 3:49:51 | 0:03:21 | 506.6 |  |
| 12/28/11 9:49:28 | 12/28/11 9:52:44 | 0:03:16 | 666.3 |  |
| 12/30/11 15:57:28 | 12/30/11 16:00:20 | 0:02:52 | 933.71 |  |

RUC Commitments

| Weather Zone | Unit Days |
| --- | --- |
| FAR WEST | 2 |
| SOUTH CENTRAL | 1 |
| Grand Total | 3 |

SCED Congestion Management Activity Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Paint Creek - Aspermont 138 kV | Aspermont 138/69 kV XFMR1 | 17 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 15 |
| Gila - Nueces Bay 138 kV | Gila - Hiway 9 138 kV | 15 |
| Pelican - White Point 138 kV | Agave - Lon Hill 138 kV | 9 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 8 |
| Whitepoint 345/138 kV XFMR | Pelican - Lon Hill 138 kV | 7 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 5 |
| Pawnee - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 3 |
| Ajo - Riohondo 345 kV | Nelson Sharpe - Celanese Bishop 138 kV | 3 |
| Nicole - Oak Creek AEP 138 kV | Nicole - Orient 138 kV | 3 |
| DCKT Tricorner - Tyler Grand & Martin Lake SES - Elkton 345 kV | Elkton - Tyler Southwest 138 kV | 3 |
| Scurry Switch - Spur 138 kV | Aspermont AEP - Aspermont Continental 69 kV | 3 |
| Weil Tract to Lon Hill 138 kV | Clarkwood - Lon Hill 138 kV | 3 |
| Pawnee - Lon Hill 345 kV | Rincon - Bonnieview 69 kV | 2 |
| Ajo - Riohondo 345 kV | Kleberg AEP - Celanese Bishop 138 kV | 2 |
| Lon Hill - North Edinburg 345 kV | North Edinburg - Rachal 138 kV | 2 |
| DCKT Watermill - Tricorner & Trinidad SES 345 kV | Trinidad SES 345/138 kV AT6 | 2 |
| Sigmor to San Miguel 138 kV | Casa Blanca - Orange Grove Switching Station 69 kV | 2 |
| DCKT Odessa EHV Switch - Morgan Creek & Quail Switch 345 kV | Stanton East - Martin Capacitor 69 kV | 2 |
| DCKT Morgan Creek SES - Bitter Creek & Sweetwater Cogen 345 kV | Tonkawa Switch - Morgan Creek SES 345 kV | 2 |
| Coleman Lake Ivie Tap - Ballinger | Ballinger - Humble Ballinger 69 kV | 2 |
| Whitepoint - Lon Hill 345 kV | Pelican - Lon Hill 138 kV | 2 |
| Big Brown SES-Richland Chambers 345 kV | Trinidad SES 345/138 kV AT6 | 2 |
| North Edinburg 345/138 kV AXFMR2 | North Edinburg 345/138 kV AXFMR1 | 2 |
| Lago Vista - Marshall Ford 138 kV | Buttercup - Whitestone 138 kV | 2 |
| DCKT Koch Up River - Nueces Bay 138 kV | Clarkwood - Lon Hill 138 kV | 2 |
| Alice - Kingsville 138 kV | Falfurrias 138/69 kV XFMR | 2 |
| DCKT Tricorner - Tyler Grand & Martin Lake SES - Elkton 345 kV | Tyler Grande 345/138 kV XFMR | 2 |
| Pawnee - Lon Hill 345 kV | Casa Blanca - Orange Grove Switching Station 69 kV | 1 |
| Lon Hill - North Edinburg 345 kV | Lon Hill - Kingsville 138 kV | 1 |
| DCKT Watermill - Tricorner & Trinidad SES 345 kV | Trinidad SES 345/138 kV AT6 | 1 |
| Sigmor to San Miguel 138 kV | San Miguel Tap - North Calliham 69 kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Albany - Hubbard BSTR 1 Tap 69 kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Sonora - Friess Ranch 69 kV | 1 |
| Lost Pines - Austrop 345 kV | Austrop 345/138 kV AXFMR | 1 |
| West Levee Switch - Watermill Switch 345 kV | Watermill Switch - Cedar Hill Switch 345 kV | 1 |
| Friend Ranch 138/69 kV AXFMR | Sonora 138/69 kV AXFMR | 1 |
| DCKT Big Brown SES - Venus Switch 345 kV | Jewet - Rattlesnake Road Switch 345 kV | 1 |
| Kock Hearns Ferry - Koch Up River 69 kV | Koch Up River 138/69 kV AXFMR | 1 |
| DCKTWatermill Switch - West Levee Switch & Sargent Road 345 kV | Cedar Hill Switch - Watermill 345 kV | 1 |
| Big Brown SES-Richland Chambers 345 kV | Trinidad SES 345/138 kV AT6 | 1 |
| Rodd Field - Holly 138 kV | Airline - Cabaniss 138 kV | 1 |
| Lon Hill - Koch Hearns Ferry 138 kV | Air Liquid AEP - Hiway9 69 kV | 1 |
| DCKT Lytton Springs - Holman & Fayette Power Plant 345 kV | Austrop 345/138 kV AXFMR | 1 |
| Lon Hill - Nelson Sharpe 345 kV | Kleberg - Celanese Bishop 138 kV | 1 |
| Nelson Sharpe - Ajo 345 kV | Harlingen Switch - Raymondville 69 kV | 1 |
| Lon Hill - Orange grove Switching Station 138 kV | Sinton - Skidmore 138 kV | 1 |
| DCKT Tradinghouse SES - Venus Switch 345 kV | Jewet - Rattlesnake Road Switch 345 kV | 1 |
| DCKT Jewett - Singleton 345 kV | Jack Creek - Tonkawa Switch 345 kV | 1 |
| Sun Switch - Golden Switch 138 kV | Bluff Creek Switch - China Grove Switch 138 kV | 1 |
| San Angelo Red Creek - Twin Buttes 345 kV | Twin Buttes 345/138 kV AXFMR | 1 |
| Willow Valley Switch - Lamesa 138 kV | Lamesa - Sparenburg 69 kV | 1 |
| Ingleside DuPont - Ingleside Cogenswitch 138 kV | Ingleside DuPont - Ingleside Cogenswitch 138 kV | 1 |
| Nueces Bay - White Point 138 kV | Pelican - Lon Hill 138 kV | 1 |
| Weslaco Switch - North Weslaco 138 kV | Weslaco Switch - Weslaco 138 kV | 1 |
| San Angelo Red Creek - Bluff Creek 345 kV | Nicole - Oak Creek AEP 138 kV | 1 |
| Victoria 138/69 kV AXFMR2 | Bonnie view - Rincon 69 kV | 1 |
| DCKT Monticello - Allen Switch & Sulphur Springs - Royse Switch 345 kV | Monticello - Farmersville 345 kV | 1 |
| San Miguel 345/138 kV AXFMRT | San Miguel 345/138 kV AXFMRH | 1 |
| DCKT Singleton - Zenith 345 kV | Singleton - Tomball 345 kV | 1 |
| Scurry - Sun Switch 138 kV | Aspermont AEP - Spur 138 kV | 1 |
| DCKT Bell County East - Sandow Switch 345 kV | Austrop 345/138 kV AXFMR | 1 |
| Paloduro - Pearsall 138 | Pearsall 138/69 kV XFMR | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 18 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 12/14/2011 | Transmission and Security Desk V1 Rev 13 | 574 |
| 12/14/2011 | Shift Supervisor Desk V1 Rev 10 | 573 |
| 12/14/2011 | Resource Desk V1 Rev 12 | 572 |
| 12/14/2011 | Reliability Unit Commitment V1 Rev 12 | 571 |
| 12/14/2011 | Real Time Desk V1 Rev 13 | 570 |
| 12/14/2011 | DC Tie Desk V1 Rev11 | 569 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

12/29 17:38   ERCOT issued an emergency notice for SCED failure. The notice was cancelled at 17:47. SCED failed for the 17:30 and 17:35 SCED runs.

Communication Issues

None

## ERCOT peak (Unofficial)

12/07 08:00 50,088 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | 3.46 |
| March | 3.29 | 3.24 | 2.24 | 2.02 |
| April | 2.45 | 2.66 | 2.47 | 3.55 |
| May | 3.01 | 2.90 | 2.63 | 3.27 |
| June | 2.81 | 2.89 | 2.84 | 2.28 |
| July | 2.55 | 2.83 | 2.39 | 1.63 |
| August | 3.66 | 3.07 | 2.29 | 2.28 |
| September | 4.99 | 3.68 | 3.14 | 2.70 |
| October | 2.79 | 2.92 | 2.37 | 3.51 |
| November | 2.60 | 1.93 | 3.46 | 3.38 |
| December | 4.54 | 3.70 | 2.60 | 2.99 |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.83 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 12/01/2011 | 11:35 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW.. |
| 12/02/2011 | 09:05 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/02/2011 | 09:39 | ERCOT issued a Watch for PRC below 2500 MW. |
| 12/02/2011 | 15:07 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1800 2000. |
| 12/03/2011 | 09:09 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1100 1300. |
| 12/03/2011 | 09:25 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/10/2011 | 17:49 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/14/2011 | 17:15 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1900 2300. |
| 12/14/2011 | 17:40 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/17/2011 | 02:40 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0900 1100. |
| 12/24/2011 | 12:00 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1800 2200. |
| 12/24/2011 | 18:04 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/25/2011 | 05:25 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0900 1300. |
| 12/25/2011 | 09:12 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 12/27/2011 | 02:39 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0800 1200. |

Transmission Watch

None

Watch

None

Emergency Notice

None

Texas RE Event Analysis

None