ERCOT Operations Report

Nov 2011 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 11/6/2011 23:06 | 59.788 | 476 | As a residual to DST change, STLF became zero for the 25th hour. A defect has been logged to fix this STLF issue. |
| 11/6/2011 23:18 | 60.108 | 4 | As a residual to DST change, STLF became zero for the 25th hour. A defect has been logged to fix this STLF issue. |
| 11/10/2011 7:56 | 59.870 | 8 | Unit trip with 420 MW net. |
| 11/14/2011 16:15 | 59.885 | 12 | Unit trip with 560 MW net. |
| 11/14/2011 21:01 | 59.835 | 377 | Gen Deviation -550 MW in 3 mins. Out of DRS. |
| 11/16/2011 13:18 | 59.826 | 56 | Unit trip with 617 MW net. |
| 11/17/2011 15:13 | 59.870 | 28 | Unit trip with 388 MW net. |
| 11/18/2011 2:41 | 59.881 | 40 | Unit trip with 442 MW net. |
| 11/18/2011 23:50 | 59.867 | 24 | Unit trip with 419 MW net. |
| 11/20/2011 14:04 | 59.812 | 76 | Unit trip with 780 MW net. |
| 11/22/2011 2:34 | 59.869 | 48 | Unit trip with 360 MW net. |
| 11/29/2011 3:29 | 59.732 | 25 | Unit trip with 1365 MW net. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 11/6/11 23:10:27 | 11/6/11 23:16:24 | 0:05:57 | 800 |  |
| 11/14/11 21:03:30 | 11/14/11 21:08:26 | 0:04:56 | 240.64 |  |

RUC Commitments

| Weather Zone | Unit Days |
| --- | --- |
| COAST | 1 |
| FAR WEST | 3 |
| NORTH | 28 |
| SOUTH | 1 |
| Grand Total | 33 |

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| DCKT Graham SES - Long Creek 345 kV | Paint Creek - Murray 138 kV | 16 |
| Paint Creek - Aspermont 138 kV | Aspermont 138/69 kV XFMR1 | 13 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 9 |
| Pelican - Whitepoint 138 kV | Pelican - Lon Hill 138 kV | 9 |
| Abilene Mulberry Creek - Oklaunion 345 kV | Lake Pauline - Vernon 138 kV | 5 |
| Basecase | Enas - WKN_BKR 69 kV | 4 |
| Scurry Switch - Sun Switch 138 kV | Spur - Aspermont 138 kV | 4 |
| Pelican - Papalote Creek 138 kV | Pelican - Lon Hill 138 kV | 4 |
| Amoco North Cowden - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 4 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 3 |
| Pawnee - San Miguel 345 kV | Pawnee 345/138 KV AT | 3 |
| DCKT Elmcreek - San Miguel 345 kV | Moore - Hondock 138 kV | 3 |
| Centerville Road Switch 345/138 kV AXFMR | Mesquite West - Mesquite East 138 kV | 3 |
| Lon Hill - White Point 345 kV | Pelican - Lon Hill 138 kV | 3 |
| George West Switching Station - Orange Grove Switching Station 138 kV | Orange Grove 69 Sub - Casa Blanca 69 kV | 3 |
| Basecase | Sonora - Cauthorn 138 kV | 2 |
| DCKT Graham SES - Long Creek 345 kV | Seymour - Bomarton 69 kV | 2 |
| DCKT Odessa High Voltage - Morgan Creek SES &Quail Switch 345 kV | Forsan Tap - Crmwd 7 Tap 138 kV | 2 |
| Sun Switch - Morgan Creek SES 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |
| Chambers - Baytown Energy Center 345 kV | Baytown Energy Center 345/138 kV AT2 | 2 |
| Seagoville 345/138 kV AXFMR2 | Forest Grove Switch - Mabank Tap 138 kV | 2 |
| Golden Switch - Sun Switch 138 kV | China Grove Switch - Bluff Creek Switch 138 kV | 2 |
| San Angelo Red Creek - Twinbute 345 kV | San Angelo Red Creek 345/138 kV XFMR2 | 2 |
| Bluff Creek Switch - China Grove Switch | Golden Switch - Brand (ONCOR) 138 kV | 2 |
| Basecase | TH Wharton XT4D | 1 |
| Basecase | TH Wharton XT4A | 1 |
| DCKT Graham SES - Long Creek 345 kV | Albany Foundry - Hubbard BSTR 1 Tap 69 kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Putnam - Moran AEP 69 kV | 1 |
| DCKT Graham SES - Long Creek 345 kV | Putnam 138/69 kV XFMR | 1 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 1 |
| Pawnee Switch - San Miguel 345 kV | Pawnee 345/138 KV AT | 1 |
| DCKT Odessa High Voltage - Morgan Creek SES &Quail Switch 345 kV | Stanton East Switch - Martin Capacitor 69 kV | 1 |
| DCKT Odessa High Voltage - Morgan Creek SES &Quail Switch 345 kV | Mc Donald Road - Forsan Tap 138 kV | 1 |
| DCKT Elmcreek - San Miguel 345 kV | Blessing - Lolita 138kV | 1 |
| Sun Switch - Morgan Creek SES 138 kV | Snyder138/69 kV AXFMR | 1 |
| Pawnee - Lon Hill 345 kV | Rincon - Air Co 138 kV | 1 |
| Pawnee - Lon Hill 345 kV | Sinton - Skidmore 69 kV | 1 |
| Getty Vealmoor - Big Spring Switch 138 V | Big Spring Switch 138/69 kV XFMR | 1 |
| Getty Vealmoor - Big Spring Switch 138 V | Big Spring Switch - Cosden 138 kV | 1 |
| SCKT Abilene Mulberry Creek - Bluff Creek 345 kV | Nicole - Oak Creek AEP 138 kV | 1 |
| Morgan Creek 345/138 kV AXFMR4 | Morgan Creek SES 345/138 XFMR 2H | 1 |
| Lane City Pump - Lane City 138 kV | Lane City - Blessing 138 kV | 1 |
| Coleman Lake Ivie tap - Ballinger 138 kV | Santa Anna Tap - Dressy 69 kV | 1 |
| Formosa 138/69 kV XFMR TR22 | Formosa 138/69 kV XFMR TR21 | 1 |
| San Angelo Red Creek - Comanche Switch 345 kV | Brownwood Switch - Camp Bowie 138 kV | 1 |
| Ennis Creek Switch - Brand 138 kV | Snyder - Amoco Tap 69 kV | 1 |
| DCKT GBY - Gable & Hardy - Crocket 345 kV | Garrott - Midtown 138 kV | 1 |
| DCKT Austrop - Lost Pines 345 kV | Fayetteville 345/138 kV AT2 | 1 |
| DCKT Ball Park - JT Deely & JT Dee 138 kV | Calaveras - Streich 138 kV | 1 |
| Ajo - Riohondo 345 kV | Raymondville 2 - Raymondville Tap 138 kV | 1 |
| DCKT Tradinghouse SES - Venus Switch 345 kV | Big Brown SES - Jewet 345 kV | 1 |
| Mc Donald Road - Big Springs Switch 138 kV | Mc Donald Road - Morgan Creek SES 345 kV | 1 |
| Whitepoint 345/138 kV XFMR | Pelican - Lon Hill 138 kV | 1 |
| DCKT Allen Switch - Royse Switch & Monticello SES 345 kV | Seagoville Switch - Kleberg 138 kV | 1 |
| Rodd Field - Barney Davis 138 kV | Airline - Cabaniss 138 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 20 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 11/01/2011 | Transmission and Security Desk V1 Rev12 | 568 |
| 11/01/2011 | Shift Supervisor V1 Rev9 | 567 |
| 11/01/2011 | Reliability Unit Commitment V1 Rev11 | 566 |
| 11/01/2011 | Resource Desk V1 Rev11 | 565 |
| 11/01/2011 | Real Time Desk V1 Rev12 | 564 |
| 11/01/2011 | Dc Tie Desk V1 Rev10 | 563 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

11/23 12:41	ERCOT issued a Transmission Watch due to large voltage swings in Wilbarger        area due to a planned outage.

Application Issues

None

Communication Issues

None

## ERCOT peak (Unofficial)

11/28 08:00 41,365 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2008 | 2009 | 2010 | 2011 |
| January | 3.30 | 4.11 | 3.78 | 2.91 |
| February | 3.59 | 3.49 | 3.79 | 3.46 |
| March | 3.29 | 3.24 | 2.24 | 2.02 |
| April | 2.45 | 2.66 | 2.47 | 3.55 |
| May | 3.01 | 2.90 | 2.63 | 3.27 |
| June | 2.81 | 2.89 | 2.84 | 2.28 |
| July | 2.55 | 2.83 | 2.39 | 1.63 |
| August | 3.66 | 3.07 | 2.29 | 2.28 |
| September | 4.99 | 3.68 | 3.14 | 2.70 |
| October | 2.79 | 2.92 | 2.37 | 3.51 |
| November | 2.60 | 1.93 | 3.46 | 3.38 |
| December | 4.54 | 3.70 | 2.60 | NA |
| Annual Average | 3.29 | 3.11 | 2.83 | 2.82 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 11/4/2011 | 00:33 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0800 - 1000 |
| 11/6/2011 | 07:19 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 10 -22 |
| 11/6/2011 | 07:20 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 10:00 22:00 |
| 11/10/2011 | 01:28 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 0800 -1100 |
| 11/12/2011 | 08:54 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 11:00 19:00 |
| 11/13/2011 | 16:18 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 11/13/2011 | 16:48 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 1900-2200 |
| 11/14/2011 | 08:42 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 11/29/2011 | 06:23 | ERCOT issued an Advisory due to PRC below 3000 MW. |
| 11/30/2011 | 06:43 | ERCOT issued an Advisory due to PRC below 3000 MW. |

Transmission Watch

11/23 12:41	ERCOT issued a Transmission Watch in Wilbarger area due to a planned outage.

Watch

11/28 06:04     ERCOT issued a Watch at 06:04 making notification for the large change in North – Houston interface from the GTL posting.

Emergency Notice

None

Texas RE Event Analysis

11/29 03:29	ERCOT experience a loss of a generating unit resulting in a loss of 1365 MW due to generator relay lock out. Frequency declined to 59.694 Hz. Investigation is currently on-going.