## Slide 1: Cross Valley 345 kV Project
Jeff Billo
Manager, Mid-Term Planning

## Slide 2: Cross Valley Background
Brownsville area is served by (4) 138 kV lines and the Silas Ray plant (~120 MW)
Brownsville Public Utility Board (BPUB) projects 250 MW of industrial load additions at the Port of Brownsville

## Slide 3
RPG Review
Sharyland Utilities (SU) and BPUB proposed Cross Valley 345 kV project to address normal load growth in East Valley, Port of Brownsville industrial load additions, and maintenance outage issues
RPG participants could not come to consensus about appropriateness of including new 250 MW industrial load addition in the study case (modeled at Loma Alta 138 kV substation)
ERCOT performed Independent Review of project
  Analysis conducted with and without 250 MW load addition
  Analysis focused on steady-state reliability needs in 2016
  Long-term (2020) sensitivity analysis performed

## Slide 4: Independent Review Reliability Analysis
Without 250 MW load additions there was one N-0 thermal violation and multiple N-1 violations for 2016:

## Slide 5: Independent Review Reliability Analysis
With 250 MW load additions there were multiple N-0 and N-1 thermal violations for 2016:

## Slide 6: Reliability Analysis: N-1-1
Multiple N-1-1 (Category C) contingency overloads
  Highest post-contingency overload is 167.2% of emergency rating (12 lines loaded >120%) - without 250 MW load additions
  Load shed allowed under NERC and ERCOT planning criteria for Category C contingency events, but exposure and extent of load shed is not practical or desirable
~175 MW would need to be shed following the first contingency
Additional ~190 MW would need to be shed following the second contingency
80% (290 MW) of the 365 MW total load shed needed for N-1-1 would be in the shaded area
2016 peak in this shaded area is 627 MW

## Slide 7: N-1-1 Load Shed Exposure
Cross Valley 345 kV line needed to reduce N-1-1 load shed risk
2016 load duration curve for Brownsville area showing N-1-1 load shed threshold
2010-11 actual daily peaks for Brownsville area

## Slide 8: Long Term Considerations
2020 ERCOT Long Term Study DOE case analyzed to determine long-term reliability needs in Valley
Results showed multiple west Valley 138 kV line overloads or near overloads under G-1 + N-1 conditions
A North Edinburg to South McAllen 345 kV line would solve most of these constraints
  Resolves ~ $95M worth of 138 kV line upgrades
Conclusion:
  Any Cross Valley 345 kV line should be routed in proximity to South McAllen to account for long term needs in the west Valley area

## Slide 9: Port of Brownsville Industrial Load Additions
RPG did not come to consensus about appropriateness of including the 250 MW industrial load additions in the study case
  BPUB and Brownsville Economic Development Council (BEDC) indicated that load modeled is representative of previous industrial customer projects that have chosen to locate elsewhere due to lack of electric infrastructure in area
    Has occurred multiple times according to BEDC
  TIEC commented that it would be inappropriate to plan transmission facilities for the addition of “speculative future loads”
TDSPs have responsibility for providing forecasts of discrete load addition assumptions in ERCOT planning models
  ERCOT performs system-wide forecasts
  ERCOT has not historically judged the validity of specific load additions
250 MW load addition in Port of Brownsville assumed in ERCOT’s recommendation, while providing a sensitivity performed without it

## Slide 10: Study Conclusions
Transmission improvements are needed to support normal load growth in Brownsville area (without the 250 MW load)
345 kV source from the west side to the east side of the Valley needed to limit N-1-1 load shed exposure to manageable levels
  Any Cross Valley 345 kV line should be routed in proximity to South McAllen to account for long-term needs in the west Valley area
Multiple alternatives studied
  “Option 5” determined to be best alternative, assuming the industrial load additions in Brownsville:
    Construct a new La Palma-Palo Alto 138 kV line (~12 miles) on new ROW with a rating of at least 215 MVA
    Construct a new North Edinburg-Loma Alta 345 kV line (double circuit capable with one circuit in place) routed in proximity to the existing South McAllen Substation (~106.5 miles ) on new ROW
    Construct a new 345kV bus at the Loma Alta station with one 345/138kV autotransformer
    Cost estimate = $274.7M

## Slide 11: Option 5

## Slide 12: Port of Brownsville Industrial Load Additions Sensitivity
If Port of Brownsville load additions were not assumed, Option 4 determined to be best option for resolving reliability needs:
    Construct a new La Palma-Palo Alto 138 kV line (~12 miles) on new ROW with a rating of at least 215 MVA
    Construct a new North Edinburg-La Palma 345 kV line (double circuit capable with one circuit in place) routed in proximity to the existing South McAllen Substation(~ 89.9 miles ) on new ROW
    Cost estimate = $234.8M

## Slide 13: Board of Director Endorsement
ERCOT will request the ERCOT BOD endorse the following improvements associated with Option 5:
    Construct a new La Palma-Palo Alto 138 kV line (~12 miles) on new ROW with a rating of at least 215 MVA
    Construct a new North Edinburg-Loma Alta 345 kV line (double circuit capable with one circuit in place) routed in proximity to the existing South McAllen Substation (~106.5 miles ) on new ROW
    Construct a new 345kV bus at the Loma Alta station with one 345/138kV autotransformer
    Cost estimate = $274.7M
ERCOT will also ask that the BOD deem the North Edinburg-Loma Alta 345 kV line critical to reliability in accordance with PUCT Substantive Rule 25.101 (b)(3)(D)
  In order to expedite the construction of the line to reduce the N-1-1 reliability risk

## Slide 14
Questions?