## Slide 1: Updates to the 2012 Methodology for Determining Ancillary Service Requirements
David Maggio
ERCOT

## Slide 2: AS Methodology Updates
During discussions at PUCT and RDTF meetings, it was proposed that ERCOT reduce the amount of NSRS that is required by 500 MW and increase the amount of RRS that is required by 500 MW
In response to that proposal, an updated version of the ERCOT Methodologies for Determining Ancillary Service Requirements document has been drafted
The changes to RRS are summarized as:
  The minimum RRS requirement will change from 2300 MW to 2800 MW
  The RRS requirement will no longer consider the forecasted Reserve Discount Factor (RDF)

## Slide 3: AS Methodology Updates
The changes to NSRS are summarized as:
  The NSRS calculation:
Base NSRS Req. = 95th Percentile of Net-Load Forecast Error – Avg. Reg. Up Req.
becomes
Base NSRS Req. = 95th Percentile of Net-Load Forecast Error – Avg. Reg. Up Req. – 500MW of RRS
  The cap for NSRS will decrease from 2000 MW to 1500 MW
  The floor for NSRS during on-peak hours (7-22) will now be equal to the single largest unit in ERCOT minus 500 MW