## Slide 1: PDCWG Report to ROS
December 8, 2011
Sydney Niemeyer

## Slide 2: ERCOT Frequency Control Performance
November, 2011

## Slide 5
Rolling 12 month average CPS1 = 147.22

## Slide 8
RMS1 Data through Dec 6, 2011

## Slide 9
RMS1 Data through Dec 6, 2011

## Slide 10
RMS1 Data through Dec 6, 2011

## Slide 16: Recent Frequency Response Performance

## Slide 18: PDCWG Meeting Nov 30th.
Intermittent Renewable Resources Primary Frequency Response (PFR):
  Reviewed one IRR PFR to normal frequency movement and during the 11-29-11 DCS event.
    Governor set per BAL-001-TRE
    Performance exceeded R9 and R10 using NDC.
    Response to normal frequency movement observed.
    Concerns with excessive wear.
BAL-001-TRE field trial.
  Participants will be selected Dec 12 during Drafting Team meeting.
  December 10th deadline to nominate generators.
Reviewed Nov 14, 21:00 low frequency event.
  Six QSEs did not follow Generator shutdown procedure as described in the ERCOT Business Practice Manual, “ERCOT And QSE Operations Practices During The Operating Hour”.
Reviewed Nov 29, 03:29 DCS event.
  Three Resources did not sustain PFR.
  Overall performance was strong and above average for PFR and Secondary Control.

## Slide 19: On Going Work
BAL-003 Field Trial
  Completing evaluation of 61 events for the 2012 ERCOT Bias calculation.
  Completing evaluation of ERCOT Interconnection Frequency Response Performance as part of the field trial.
  Evaluation will be completed by December 15th.

## Slide 20: PDCWG Next Meetings
January 4th Met Center 9:00 am to 5:00 pm.
February 1st Met Center 9:00 am to 5:00 pm.