| NPRR Number | 434 | NPRR Title | Increase the Capacity Limitation of a Generation Resource Providing RRS |
| --- | --- | --- | --- |
| Date |  | January 12, 2012 |  |
| Submitter’s Information |  |  |  |
| Name |  | Isabel Flores / Sandip Sharma |  |
| E-mail Address |  | iflores@ercot.com / ssharma@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6531 / 512-248-4298 |  |
| Cell Number |  | 512-565-9117/817-371-7773 |  |
| Market Segment |  | Not applicable. |  |

Comments

ERCOT in part agrees with the 01/10/12, PDCWG comments and requests that the sponsor of this Nodal Protocol Revision Request (NPRR) provide the technical basis for increasing the current 20% requirement to 28% other than aiming to keep the unit commitment at same level.   The “20%” requirement technical support is based on Governor action for protecting the under-frequency Load shedding relay setting that occurs at 59.30 Hz.  This threshold also ensures proper distribution of Responsive Reserve (RRS) amongst the Resources qualified to provide RRS in the ERCOT market.  ERCOT believes that raising the threshold to 28% not only severs the relationship between the 5% Droop, 20% of High Sustained Limit (HSL), and a 1% change in frequency but it degrades the quality of a reliability tool.

Furthermore, this NPRR aims to reduce the number of Generators which will carry the 1400 MW RRS and has ignored the actual deliverability of the service.  While ERCOT has the ability to initiate a Secondary Ancillary Services Market (SASM) to replace MWs that are not provided it takes a minimum of two hours to run a SASM for a product that is supposed to respond within ten minutes.

Since this NPRR is the result of 500 MW of Non-Spin Reserve (Non-Spin) being moved to RRS it also reduces the number of Resources providing Non-Spin.  ERCOT also believes that the 28% allocation will yield higher RRS concentrations in areas where the service is not deliverable.  ERCOT also recommends that distribution of RRS responsibility on a geographic basis be considered and reiterates that while a SASM may be initiated the timing may not be appropriate during an event.

ERCOT has added a provision to perform unannounced RRS testing in order to verify that the RRS responsibility carried by Resources is achievable.  Additionally, ERCOT proposes to limit Resources that fail unannounced testing to what they can actually provide for a minimum period of 90 days at which time re-testing can be scheduled. These comments also include proposed changes to Section 3.17.2, Responsive Reserve Service

ERCOT would also like to add that, any changes from existing practice will require system changes.

Revised Proposed Protocol Language

3.16	Standards for Determining Ancillary Service Quantities

(1)	ERCOT shall comply with the requirements for determining Ancillary Service quantities as specified in these Protocols and the ERCOT Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the minimum quantity requirements for each Ancillary Service needed for reliability, including the percentage of Load Resources excluding Controllable Load Resources, the percentage of DC Tie, and the percentage of Controllable load Resources allowed to provide Responsive Reserve Service (RRS) calculated on a monthly basis.

(3)	The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements and the monthly percentage of Load Resources, Controllable Load Resources and DC Ties allowed to provide RRS.

(4)	If ERCOT determines a need for additional Ancillary Service Resources under these Protocols or the ERCOT Operating Guides, after an Ancillary Service Plan for a specified day has been posted, ERCOT shall inform the market by posting notice on the MIS Secure Area, of ERCOT’s intent to procure additional Ancillary Service Resources under Section 6.4.8.2, Supplemental Ancillary Service Market.  ERCOT shall post the reliability reason for the increase in service requirements.

(5)	ERCOT shall post engineering studies on the MIS Secure Area representing specific Ancillary Service requirement on an annual basis.

(6)	The amount of Load Resources on high-set under-frequency relays providing RRS is limited to 50% of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed.

(7)	The amount of RRS that a QSE can self-arrange using a Load Resource excluding Controllable Load Resources is limited to the lower of:

(a)	fifty percent (50%) of its RRS Obligation, or

(b)	a reduced percentage of its RRS Obligation based on the limit established by ERCOT in paragraph (6) above.

(8)	However, a QSE may bid more of the Load Resource above the percentage limit established by ERCOT for sale of RRS to other Market Participants.  The total amount of Responsive Reserve Service using the Load Resource excluding Controllable Load Resources procured by ERCOT is also limited to the lesser of the 50% limit or the limit established by ERCOT in paragraph (6) above.

(9)	ERCOT shall update the RRS threshold %, defined in the Ancillary Service Methodology in the event that the total amount of RRS procured changes.  RRS must have minimum of 1150 MW of Primary Frequency Response which is maintained by Generation Resources capable of responding with a 5% droop for a 1% change in frequency.

3.17.2	Responsive Reserve Service

(1)	Responsive Reserve (RRS) Service is a service used to restore or maintain the frequency of the ERCOT System:

(a)	In response to, or to prevent, significant frequency deviations;

(b)	As backup Regulation Service; and

(c)	By providing energy during an Energy Emergency Alert (EEA).

(2)	RRS may be provided through one or more of the following means:

(a)	By using frequency-dependent response from On-Line Resources as prescribed in the Operating Guides to help restore the frequency within the first few seconds of an event that causes a significant frequency deviation in the ERCOT System; and

(b)	Either manually or by using a four-second signal to provide energy on deployment by ERCOT.

(3)	RRS Service may be used to provide energy during the implementation of an EEA.  Under the EEA, RRS provides generation capacity, capacity from Controllable Load Resources or interruptible Load available for deployment on ten minutes’ notice.

(4)	Responsive Reserve (RRS) Service may be provided by:

(a)	Unloaded, On-Line Generation Resource capacity;

(b)	Load Resources controlled by high-set, under-frequency relays;

(c)	Controllable Load Resources;

(d)	Hydro Responsive Reserves as defined in the Operating Guides; and

(e)	Direct Current Tie (DC Tie) response that stops frequency decay as defined in the Operating Guides.

(5)	ERCOT shall ensure that RRS is not concentrated in any Congestion Management Zone (CMZ) at a quantity greater than 40% of the total amount of RRS procured.

- 3.18	Resource Limits in Providing Ancillary Service

(1)	For both Generation Resources and Load Resources the High Sustained Limit (HSL) must be greater than or equal to the Low Sustained Limit (LSL) and the sum of the Resource-specific designation of capacity to provide Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), and Non-Spinning Reserve (Non-Spin).

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

(3)	For RRS Service:

(a)	The full amount of RRS provided from a Generation Resource must be less than or equal to a percent  of thermal a unit’s HSL for an Ancillary Service Offer must be less than or equal to ten times the Emergency Ramp Rate, and must be frequency responsive.  The RRS allocation is defined in the ERCOT Ancillary Services Methodology;

(b)	Hydro Generation Resources operating in the synchronous condenser fast-response mode may provide RRS up to the hydro Generation Resource’s proven 20-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay setting shall not be lower than 59.80 Hz;

(c)	For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 24% of the HSL; and

(d)	The amount of RRS provided from a Load Resource must be less than or equal to the HSL minus the sum of the LSL, Reg-Up Resource Responsibility, Reg-Down Resource Responsibility, and Non-Spin Resource Responsibility.

(4)	ERCOT may conduct an unannounced test to verify that the RRS responsibility carried by a Resource is achievable.  A Resource must respond by increasing its generation to an amount equivalent to its RRS responsibility within ten minutes of the issuance of a Verbal Dispatch Instruction (VDI).  In the event a Resource fails to meet its RRS responsibility, the Resource will be limited to the capacity that it was able to reach within ten minutes for a minimum period of 90 days.  During the 90-day period, the Resource must provide ERCOT with a corrective action plan, which addresses the issues that caused the Resource to fail the unannounced test.  After the Resource has implemented a corrective action plan to ERCOT’s satisfaction, a re-test may be scheduled.