## Slide 1: Updates to the 2012 Methodology for Determining Ancillary Service Requirements
TAC Meeting
Feb. 2, 2012

## Slide 2: Origin of Methodology Changes
During discussions at PUCT and RDTF meetings, it was proposed that ERCOT reduce the amount of NSRS that is required by 500 MW and increase the amount of RRS that is required by 500 MW
In response to that proposal, an updated version of the ERCOT Methodologies for Determining Ancillary Service Requirements document was drafted to accomplish that 500 MW transfer between services

## Slide 3: Responsive Reserve Service
The changes to RRS are summarized as:
  The minimum RRS requirement will change from 2300 MW to 2800 MW
  The RRS requirement will no longer consider the forecasted Reserve Discount Factor (RDF)
The language in the document currently allows up to 50% of the requirement to be provided by Load Resources which are not Controllable Load Resources
  This value is left unchanged
  This cap is being discussed as part of NPRR 434

## Slide 4: Non-Spin Reserve Service
The changes to NSRS are summarized as:
  The NSRS calculation:
Base NSRS Req. = 95th Percentile of Net-Load Forecast Error – Avg. Reg. Up Req.
becomes
Base NSRS Req. = 95th Percentile of Net-Load Forecast Error – Avg. Reg. Up Req. – 500MW of RRS
  The cap for NSRS will decrease from 2000 MW to 1500 MW
  The floor for NSRS during on-peak hours (7-22) will now be equal to the single largest unit in ERCOT minus 500 MW (875 MW)

## Slide 5: WMS and ROS Discussion
The floor for NSRS during On-peak hours was a main point of discussion during the WMS and ROS meetings
WMS and ROS recommended that the ERCOT proposed methodology be accepted with the exception that the NSRS floor during On-Peak hours be removed
  This may result in the NSRS requirement being reduced by more than 500 MW
  The RRS requirement would still only increase by 500 MW, therefore reducing the total amount of reserves
Removing the floor may result in ERCOT Operators procuring additional reserves through the DAM or a SASM
  This may lead to the NSRS requirements fluctuating from one day to the next