| NPRR Number | 424 | NPRR Title | Reactive Capability Testing Requirements for IRRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | February 2, 2012 |  |  |
| Proposed Effective Date |  | May 1, 2012 |  |  |
| Priority and Rank Assigned |  | Not applicable |  |  |
| Nodal Protocol Section Requiring Revision |  | 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification |  |  |
| Operating Guide Sections Requiring Revision |  | 3.3.2.2, Non-Coordinated Reactive Testing 3.3.2.3, Coordinated Reactive Testing |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) defines the reactive capability testing requirement for Intermittent Renewable Resources (IRRs). |  |  |
| Reason for Revision |  | In order to perform effective testing and evaluation, this NPRR proposes new parameters for IRR lagging and leading tests. IRR lagging tests are to be conducted when the IRR is generating at or above 60% of its Seasonal High Sustained Limit (HSL). Conducting lagging tests at this level will allow IRRs a more reasonable opportunity to complete lagging tests. IRR leading tests are to be performed when the IRR is generating below 60% of its Seasonal HSL. Conducting leading tests at this level will provide better evaluation of the IRRs ability to respond to voltage issues. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR424 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 11/2/11, NPRR424 and the associated Impact Analysis were posted. - On 11/14/11, Oncor Electric Delivery comments were posted. - On 11/17/11, PRS considered NPRR424. - On 12/8/11, ERCOT comments were posted. - On 12/15/11, PRS again considered NPRR424. - On 1/19/12, PRS considered the 12/15/11 PRS Report and Impact Analysis for NPRR424. - On 2/2/12, TAC considered NPRR424. |  |  |
| PRS Decision |  | On 11/17/11, PRS unanimously voted to table NPRR424. All Market Segments were present for the vote. On 12/15/11, PRS voted to recommend approval of NPRR424 as amended by the 12/8/11 ERCOT comments. There was one abstention from the Consumer Market Segment. All Market Segments were present for the vote. On 1/19/12, PRS unanimously voted to endorse and forward the 12/15/11 PRS Report as revised by PRS and the Impact Analysis for NPRR424 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 11/17/11, there was concern that the proposed changes could result in high voltage issues and that a solution may be to consider the capability curves. On 12/15/11, there was no discussion. On 1/19/12, non-substantive administrative changes were proposed. |  |  |
| TAC Decision |  | On 2/2/12, TAC unanimously voted to recommend approval of NPRR424 as recommended by PRS in the 1/19/12 PRS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 2/2/12, there was no discussion. |  |  |
| ERCOT Opinion |  | ERCOT supports the approval of NPRR424. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | Clarifies testing requirements for IRRs providing VSS. |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
|  | 5 |  |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores |
| E-mail Address | iflores@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6531 |
| Cell Number | 512-565-9117 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | 512-248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Oncor Electric Delivery 111411 | Requested an explanation on the rational for selecting the proposed MW output levels for testing. |
| ERCOT 120811 | Revised the leading test level from generating below 35% to generating below 60%. |

Comments

Please note that NPRR366, Generation Resource Power Factor Criteria Clarification, also proposes revisions to Section 8.1.1.2.1.4.

Proposed Protocol Language Revision

- 8.1.1.2.1.4	Voltage Support Service Qualification

(1)	The Resource Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources providing Voltage Support Service (VSS), as required by the Operating Guides.  Generation Resources providing VSS reactive capability limits shall be specified considering nominal substation voltage.

(2)	The Resource Entity shall conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests are performed on initial qualification and at a minimum of once every two years.  ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Resource Entity is not obligated to place Generation Resources On-Line solely for the purposes of testing.  The reactive capability tests must be conducted at a time agreed to in advance by the Resource Entity, its QSE, the applicable TSP, and ERCOT.

(3)	Maximum lagging power factor reactive operating limit must be demonstrated during peak Load Season, at or above 95% of the current Seasonal High Sustained Limit (HSL), insofar as system voltage conditions and other factors will allow.   Generation Resources that are classified as Intermittent Renewable Resources (IRRs) shall be tested when generating at or above 60% of their Seasonal HSL.  The Generation Resource providing VSS is required to maintain this level of Reactive Power for 15 minutes.

(4)	Maximum leading power factor reactive operating limit must be demonstrated during light Load conditions, with the Generation Resource operating at a typical output for that condition, or the normal expected output level for solid fuel Generation Resources during light Load conditions, insofar as system voltage conditions and other factors will allow. Generation Resources that are classified as IRRs shall be tested when generating below 60% of their Seasonal HSL. The Generation Resource is required to maintain this level of Reactive Power for 15 minutes.

(5)	The Resource Entity shall perform the AVR tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests must be performed on initial qualification.  The AVR tests must be conducted at a time agreed on in advance by the Resource Entity, its QSE, the applicable TSP and ERCOT.