ERCOT Operations Report

Jan 2012 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 1/15/2012 14:04 | 59.851 | 60 | Unit trip with 455 MW net. |
| 1/16/2012 10:48 | 59.851 | 8 | Unit trip with 257 MW net. Expected Gen Deviation -560 MW including the unit trip. |
| 1/16/2012 18:04 | 60.110 | 16 | Expected Gen Deviation +850 MW |
| 1/21/2012 13:34 | 59.752 | 152 | Unit trip with 584 MW net. |
| 1/23/2012 23:47 | 59.822 | 84 | Unit trip with 620 MW net. |
| 1/25/2012 22:04 | 59.868 | 114 | Unit trip with 186 MW net. |
| 1/25/2012 22:12 | 60.107 | 44 | Expected Gen Deviation +1500 MW. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/15/12 14:04:56 | 1/16/12 14:07:48 | 0:02:52 | 430.56 |  |
| 1/21/12 13:34:14 | 1/22/12 13:37:40 | 0:03:26 | 996.16 |  |
| 1/22/12 18:02:02 | 1/23/12 18:04:06 | 0:02:04 | 409.7 | Expected Gen Deviation -600 MW. Frequency went to 59.93 |
| 1/23/12 23:48:58 | 1/24/12 23:50:50 | 0:01:52 | 619.85 |  |
| 1/25/12 22:04:56 | 1/25/12 22:09:32 | 0:04:36 | 667.04 |  |

RUC Commitments

| Weather Zone | Unit Days |
| --- | --- |
| FAR WEST | 1 |
| SOUTHERN | 1 |
| Grand Total | 2 |

SCED Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 28 |
| Sacroc - Sun Switch 138 kV | Sun Switch - Morgan Creek SES 138 kV | 14 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 14 |
| DCKT Nueces Bay - Koch Up River & Lon Hill 138 kV | Clarkwood - Lon Hill 138kV | 11 |
| Sun Switch - Morgan Creek SES 138 kV | Sun Switch - Sacroc 138 kV | 9 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 9 |
| Wharton - Dyann 138 kV | Lane City - Blessing 138 kV | 8 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 8 |
| Basecase | Enas - WKN_BKR 69 kV | 7 |
| Bluff Creek 345/138 kV XFMR2 | Nicole - Oak Creek AEP 138kV | 6 |
| Scurry Switch - Sun Switch 138 kV | Aspermont 138/69 kV XFMR1 | 5 |
| DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 4 |
| Lobo - San Miguel 345 kV | San Diego - Freer 69 kV | 4 |
| DCKT Jewett - Singleton 345 kV | Tonkawa Switch - Jack Creek 345 kV | 4 |
| Pawnee - Lon Hill 345kV | Sinton - Skidmore 69kV | 4 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69kV | 3 |
| Basecase | Brackenville - Hamilton Road 138 kV | 2 |
| Sacroc - Sun Switch 138 kV | Aspermont 138/69 kV XFMR1 | 2 |
| DCKT Singleton - Zenith 345 kV | Tomball - Hockley 138 kV | 2 |
| DCKT Graham SES - Long Creek 345 kV | Santa Anna Tap - Dressey 69 kV | 2 |
| Lobo 345/138 kV XFMR #2 | San Diego - Freer 69 kV | 2 |
| Victoria - Coleto Creek 138 kV | Coleto Creek - Victoria 138 kV | 2 |
| Salt Creek BEPC - Spur 138 kV | Aspermont 138/69 kV XFMR1 | 2 |
| DCKT Singleton - Tomball & Roansprairie 345 kV | Zenith - TH Wharton 345 kV | 2 |
| Scurry Switch - Sun Switch 138 kV | Spur - Aspermont 138 kV | 1 |
| Lobo - San Miguel 345 kV | San Miguel 345/138 kV AXFMR | 1 |
| DCKT Graham SES - Long Creek 345 kV | Putnam 138/69 kV XFMR | 1 |
| Lobo 345/138 kV XFMR #3 | Wormser Road- Santo Nino 138 kV | 1 |
| Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Kingsville 138kV | 1 |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg 138 kV | 1 |
| DCKT Lytton Springs - Zorn & Austrop 345 kV | Turner - Buda 138 kV | 1 |
| Odessa Basin Switch - Odessa North 69 kV | Odessa North - North Cowden 69 kV | 1 |
| Weil Tract to Lon Hill 138kV | Clarkwood - Lon Hill 138kV | 1 |
| Bluff Creek Switch - China Grove Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Coleto Creek 345/138 kV XFMR2 | Victoria - Loop 463 Sub 138 kV | 1 |
| San Miguel 345/138 kV AXFMR | San Diego - Freer 69 kV | 1 |
| Gail Sub - Willow Valley Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Exxon Sharon Ridge - Willow Valley Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Pasgen - Jefferson 138 kV | Drouet - Garden Villas 138 kV | 1 |
| Citgo West - Weil Tract 138 kV | Lon Hill - Clarkwood 138 kV | 1 |
| Batesville - Paloduro 138 kV | Moore - Downies 138 kV | 1 |
| Gaf TNP- PH Robinson 138 kV | Heights TNP - PH Robinson 138 kV | 1 |
| DCKT Tonkawa Switch - Gibbons Creek & Jack Creek Switch 345 kV | Jewett - Singleton 345 kV | 1 |
| Hiway 9 - Citgo N Oak Park 138 kV | Nuesces Bay - Morris Street138 kV | 1 |
| DCKT Barney Davis - Airline & Rodd Field 138 kV | Barney Davis - Alazan 138 kV | 1 |
| Nelson Sharpe - Ajo 345kV | Falfurrias - Premont 69 kV | 1 |
| Aspermont - Paint Creek 138 kV | Aspermont 138/69 kV XFMR1 | 28 |
| Sacroc - Sun Switch 138 kV | Sun Switch - Morgan Creek SES 138 kV | 14 |
| Fort Stockton - Barilla 138 kV | Fort Stockton Switch - Barilla 69 kV | 14 |
| DCKT Nueces Bay - Koch Up River & Lon Hill 138 kV | Clarkwood - Lon Hill 138kV | 11 |
| Sun Switch - Morgan Creek SES 138 kV | Sun Switch - Sacroc 138 kV | 9 |
| Amoco North Cowden Tap - Moss Switch 138 kV | Odessa North Transformer 138/69 kV | 9 |
| Wharton - Dyann 138 kV | Lane City - Blessing 138 kV | 8 |
| Whitepoint 345/138 kV XFMR | Sinton - Skidmore 69 kV | 8 |
| Basecase | Enas - WKN_BKR 69 kV | 7 |
| Bluff Creek 345/138 kV XFMR2 | Nicole - Oak Creek AEP 138kV | 6 |
| Scurry Switch - Sun Switch 138 kV | Aspermont 138/69 kV XFMR1 | 5 |
| DCKT Singleton - Zenith 345 kV | Hockley - Betka 138 kV | 4 |
| Lobo - San Miguel 345 kV | San Diego - Freer 69 kV | 4 |
| DCKT Jewett - Singleton 345 kV | Tonkawa Switch - Jack Creek 345 kV | 4 |
| Pawnee - Lon Hill 345kV | Sinton - Skidmore 69kV | 4 |
| Orange Grove Switching Station - Lon Hill 138 kV | Sinton - Skidmore 69kV | 3 |
| Basecase | Brackenville - Hamilton Road 138 kV | 2 |
| Sacroc - Sun Switch 138 kV | Aspermont 138/69 kV XFMR1 | 2 |
| DCKT Singleton - Zenith 345 kV | Tomball - Hockley 138 kV | 2 |
| DCKT Graham SES - Long Creek 345 kV | Santa Anna Tap - Dressey 69 kV | 2 |
| Lobo 345/138 kV XFMR #2 | San Diego - Freer 69 kV | 2 |
| Victoria - Coleto Creek 138 kV | Coleto Creek - Victoria 138 kV | 2 |
| Salt Creek BEPC - Spur 138 kV | Aspermont 138/69 kV XFMR1 | 2 |
| DCKT Singleton - Tomball & Roansprairie 345 kV | Zenith - TH Wharton 345 kV | 2 |
| Scurry Switch - Sun Switch 138 kV | Spur - Aspermont 138 kV | 1 |
| Lobo - San Miguel 345 kV | San Miguel 345/138 kV AXFMR | 1 |
| DCKT Graham SES - Long Creek 345 kV | Putnam 138/69 kV XFMR | 1 |
| Lobo 345/138 kV XFMR #3 | Wormser Road- Santo Nino 138 kV | 1 |
| Nelson Sharpe - Lon Hill 345 kV | Lon Hill - Kingsville 138kV | 1 |
| Nelson Sharpe - Lon Hill 345 kV | Celanese Bishop - Kleberg 138 kV | 1 |
| DCKT Lytton Springs - Zorn & Austrop 345 kV | Turner - Buda 138 kV | 1 |
| Odessa Basin Switch - Odessa North 69 kV | Odessa North - North Cowden 69 kV | 1 |
| Weil Tract to Lon Hill 138kV | Clarkwood - Lon Hill 138kV | 1 |
| Bluff Creek Switch - China Grove Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Coleto Creek 345/138 kV XFMR2 | Victoria - Loop 463 Sub 138 kV | 1 |
| San Miguel 345/138 kV AXFMR | San Diego - Freer 69 kV | 1 |
| Gail Sub - Willow Valley Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Exxon Sharon Ridge - Willow Valley Switch 138 kV | Sparenburg - Lamesa 69 kV | 1 |
| Pasgen - Jefferson 138 kV | Drouet - Garden Villas 138 kV | 1 |
| Citgo West - Weil Tract 138 kV | Lon Hill - Clarkwood 138 kV | 1 |
| Batesville - Paloduro 138 kV | Moore - Downies 138 kV | 1 |
| Gaf TNP- PH Robinson 138 kV | Heights TNP - PH Robinson 138 kV | 1 |
| DCKT Tonkawa Switch - Gibbons Creek & Jack Creek Switch 345 kV | Jewett - Singleton 345 kV | 1 |
| Hiway 9 - Citgo N Oak Park 138 kV | Nuesces Bay - Morris Street138 kV | 1 |
| DCKT Barney Davis - Airline & Rodd Field 138 kV | Barney Davis - Alazan 138 kV | 1 |
| Nelson Sharpe - Ajo 345kV | Falfurrias - Premont 69 kV | 1 |

Generic Transmission Limits (GTL’s)

| GTL | Days |
| --- | --- |
| West – North | 26 |
| North – Houston | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

SPS (RAS) (New, Modified, Removed)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 01/19/2012 | Transmission and Security Desk V1 Rev 14 | 580 |
| 01/19/2012 | Shift Supervisor Desk V1 Rev 11 | 579 |
| 01/19/2012 | Resource Desk V1 Rev 13 | 578 |
| 01/19/2012 | Reliability Unit Commitment Desk V1 Rev 13 | 577 |
| 01/19/2012 | Real Time Desk V1 Rev 14 | 576 |
| 01/19/2012 | DC Tie Desk V1 Rev 12 | 575 |

## Load Shed Incidences

None

EEA

None

System Voltage Problems

None

Application Issues

1/07 12:46  	ERCOT issued an emergency notice for SCED failure for intervals 00:40 through 00:55. The notice was cancelled at 01:10.

Communication Issues

None

## ERCOT peak (Unofficial)

01/13 08:00 46,924 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2009 | 2010 | 2011 | 2012 |
| January | 4.11 | 3.78 | 2.91 | 2.94 |
| February | 3.49 | 3.79 | 3.46 | NA |
| March | 3.24 | 2.24 | 2.02 | NA |
| April | 2.66 | 2.47 | 3.55 | NA |
| May | 2.90 | 2.63 | 3.27 | NA |
| June | 2.89 | 2.84 | 2.28 | NA |
| July | 2.83 | 2.39 | 1.63 | NA |
| August | 3.07 | 2.29 | 2.28 | NA |
| September | 3.68 | 3.14 | 2.70 | NA |
| October | 2.92 | 2.37 | 3.51 | NA |
| November | 1.93 | 3.46 | 3.38 | NA |
| December | 3.70 | 2.60 | 2.99 | NA |
| Annual Average | 3.11 | 2.83 | 2.83 | 2.94 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | Event |
| --- | --- | --- |
| 1/5/2012 | 07:06 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/17/2012 | 18:45 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/21/2012 | 03:33 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 10:00 15:00 |
| 1/21/2012 | 08:41 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/25/2012 | 17:43 | ERCOT issued an Advisory due to Physical Responsive Capability (PRC) below 3000 MW. |
| 1/29/2012 | 06:50 | ERCOT issued an OCN for a Projected Reserve Capacity Shortage for HE 10:00 -12:00 |

Transmission Watch

1/14 02:49  	ERCOT issued a transmission watch. The notice was cancelled at 03:40.

Watch

None

Emergency Notice

SCED failure listed above in applications issues.

Texas RE Event Analysis

None