## Slide 1: PDCWG Report to ROS
<number>
February 9, 2012
Sydney Niemeyer

## Slide 2: ERCOT Frequency Control Performance
<number>
January, 2012

## Slide 3
<number>

## Slide 4
<number>

## Slide 5
<number>
12 Month Rolling Average CPS1 = 149.87

## Slide 6
<number>

## Slide 7
<number>

## Slide 8
<number>

## Slide 9
<number>

## Slide 10
<number>

## Slide 11
<number>

## Slide 12
<number>

## Slide 13
<number>

## Slide 14
<number>

## Slide 15: PDCWG Meeting Feb 1st
<number>
22 members present.
Reviewed GREDP performance.
Reviewed Jan 21, 2012 13:34 frequency event.
  Interconnection Primary Frequency Response was -394 MW/0.1 Hz below the protocol minimum of -420 MW/0.1 Hz from generators.
  Contributing causes:
    Ten Combined Cycle facilities providing RRS had low PFR performance.

## Slide 16: Jan 21, 2012 Event continued
Contributing causes continued:
  Two Conventional steam units providing RRS had low PFR performance.
  Operating Guide 2.3.1.2 (9) (c) allows Hydro Units providing RRS to be deployed manually.
  Ten Combined Cycle facilities not providing RRS had low PFR performance.
  Two simple cycle combustion turbines not providing RRS had low PFR performance.
  Several Coal fired steam units were off-line. Historically these units are good providers of PFR.

## Slide 17: Jan 21, 2012 Event
<number>

## Slide 18: PDCWG Issues with Evaluating Combined Cycle Facilities
Spinning Reserve.
  Amount provided by duct burner operation is not known.
  For multiple CT configurations, the available spinning reserve on each CT is not known. This makes calculating expected performance less accurate.
  Accuracy of HSL due to changing weather conditions throughout the day impacts expectations.
Spinning Reserve telemetry on each CT would solve most problems.

## Slide 19: PDCWG Next Meeting
<number>
February 28th Met Center 9:00 am to 5:00 pm.