## Op Guides
Check the appropriate box below. This reference uses the definition of the seasons found in the :
References to Season, Seasons, or Seasonal | Operating Guides: Summer (May 15 – September 15) Fall (September 16 – November 30) Winter (December 1 – February 28) Spring (March 1 – May 14) | Protocols: Winter- December, January, and February Spring- March, April, and May Summer- June, July, and August Fall- September, October, and November. | Other:
Table of Contents
8D Seasonal Unit Net Real Power Capability Verification
8F Seasonal Hydro Responsive Reserve Net Capability Verification
2.7.4.2 Parameters for Standard Reactor and Capacitor Switching Plan
Device Attributes
(a) Transmission Element name per Protocol Section 3.10.7.1, Modeling of Transmission Elements and Parameters;
(b) Substation name; and
(c) Schedules of device:
(i) Time-based;
(ii) Voltage-based;
(iii) Load-based;
(iv) Contingency-based;
(v) Normal Operation;
(vi) Emergency Operation;
(vii) Seasonal; and
(viii) Others as required by technology.
3.3.1 Unit Capability Requirements
(1) In the event that a QSE fails to meet Protocol Section 8.1.1.2, General Capacity Testing Requirements, requiring seasonal unit capability reporting and testing, ERCOT shall provide this QSE with notice of its failure to meet the Protocols. This notice shall be sent to the primary contact of the QSE representing the Generation Resource via e-mail. In addition to this written notice, ERCOT shall make a reasonable effort to notify the QSE via telephone.
Section 8 DEFINITIONS
Combustion Turbine Base Load = maximum Load capability for the season when frequency response test is performed
Section 8 Attachment D
Seasonal Unit Net Real Power Capability Verification
Section 8 Attachment F
Seasonal Hydro Responsive Reserve Net Capability Verification

## Protocols
Check the appropriate box below. This reference uses the definition of the seasons found in the :
References to Season, Seasons, or Seasonal | Operating Guides: Summer (May 15 – September 15) Fall (September 16 – November 30) Winter (December 1 – February 28) Spring (March 1 – May 14) | Protocols: Winter- December, January, and February Spring- March, April, and May Summer- June, July, and August Fall- September, October, and November. | Other:
SECTION 2: DEFINITIONS AND ACRONYMS
Adjusted Static Models
Load Profiles that are generated from statistical models that are based on static historical Load data, and adjusted for conditions of the day (e.g., weather, Season, etc.).
3.1.4.8 Deratings
The Resource Entity or its designee must enter material deratings that are expected to last more than 48 hours in the ERCOT Outage Scheduler. A derating is considered to be material when the Resource’s capability is reduced by 2% of its prior High Sustained Limit (HSL) for Generation Resources larger than 500 MW and 10% of its prior HSL for Generation Resources smaller than 500 MW. For QSEs representing Wind-powered Generation Resources (WGRs), the loss of a portion of the capacity shall be due to the unavailability of a portion of the equipment and shall not include capacity changes due to changes in wind speed at the WGR facility. For QSEs representing WGRs, the percentage calculation will be determined using the seasonal net maximum sustainable rating of the WGR. ERCOT will consider the Resource’s capability as the lesser of the latest seasonal Net Dependable Capability test, or the resource registration process.
3.7.1.1 Generation Resource Parameters
(2) Seasonal Resource Parameters must be submitted by a Resource Entity and must include the following for each of its Generation Resources:
(a) Seasonal gross and net MW rating;
3.14.1.7 RMR or MRA Contract Termination
(5) If ERCOT determines that a mutually agreeable preliminary construction outage schedule can be accommodated during the fall, winter, or spring, ERCOT and the TSP shall collaborate to determine if the 90 day termination notice for the RMR and/or MRA can be issued as soon after the summer load season of the preceding year as possible and publish a Market Notice of these terminations. ERCOT and the TSP may give consideration to the risk of the decision to terminate the RMR and/or MRA Agreement and any options, such as Remedial Action Plans and/or Mitigation Plans that could be used to mitigate transmission construction delays.
3.14.1.9 Generation Resource Return to Service Updates
(1) By April 1st and October 1st of each year and when material changes occur, every Resource Entity that owns or controls a Mothballed Generation Resource or an RMR Unit with an approved exit strategy shall report to ERCOT, on a unit-specific basis, the estimated lead time required for each Resource to be capable of returning to service and, in percentage terms, report probable generation capacity from each Resource that the Resource Entity expects to return to service in each Season of each of the next ten years.
5.6.1.2 Verifiable Minimum-Energy Costs
(2) The QSE must submit the Resource’s cost information by season if the Resource’s costs vary by season. For gas-fired units, the actual fuel costs must be calculated using the actual seasonal heat rate (which must be supplied to ERCOT with seasonal heat-rate test data) multiplied by the FIP * 1.X, where X = $0.50/fuel price. A new X is effective for the date(s) as described in the Verifiable Cost Manual. For coal- and lignite-fired units, the actual fuel costs must be calculated using the actual seasonal heat rate multiplied by a deemed fuel price of $1.50 per MMBtu. For fuel oil-fired operations, the number of gallons burned must be multiplied by the FOP.
6.6.9 Emergency Operations Settlement
(3) In accordance with paragraph (8) of Section 3.8.3, Quick Start Generation Resources, a QSE that represents a QSGR that comes On-Line as a result of a Base point less than its Resource Registration applicable seasonal net minimum sustainable rating shall be considered for additional compensation using the formula in Section 6.6.9.1. If the Resource Settlement Point Price at the QSGR’s Resource Node is lower than the Energy Offer Curve price, capped per the Mitigated Offer Cap pursuant to Section 4.4.9.4.1, Mitigated Offer Cap, at the aggregated Base Point during the 15-minute Settlement Interval, ERCOT shall pay the QSE additional compensation for the amount of energy from the Off-Line zero Base Point to the aggregated output level. For the purpose of this settlement, and limited to the first q Settlement Intervals inclusive of the first Settlement Interval in which the QSGR is deployed by SCED from a current SCED Base Point equal to zero MW to a Base Point greater than zero and less than the QSGR’s Resource Registration applicable seasonal net minimum sustainable rating LSL for the Operating Hour that includes the first Settlement Interval, SCED Base Points will be used in place of the Emergency Base Point.
8.1.1.2 General Capacity Testing Requirements
(1) Within the first 15 days of each Season, each QSE shall provide ERCOT a seasonal High Sustained Limit (HSL) for any Generation Resource with a capacity greater than ten MW that will be operated during that Season. ERCOT shall provide an appropriate form for QSEs to submit their seasonal HSL data. The seasonal HSL form shall take into account auxiliary Load and gross and net real power capability of the Generation Resource. Each QSE shall update its COP and telemetry, as necessary, to reflect the HSL of each of its Generation Resources in a given operating interval as well as other operational limitations. The HSL shown in the COP for a Generation Resource may not be ramp rate-limited while the Real-Time telemetered value of HSL for the Generation Resource may be ramp rate-limited by the QSE representing the Generation Resource in order for the Generation Resource to meet its HSL using the testing process described in paragraph (2) below.
(4) Should the designated Generation Resource fail to reach its HSL shown in its telemetry within the time frame set forth herein, the Real-Time averaged MW telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season. The QSE shall have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may retest up to two times per month. The QSE may also demonstrate an increased value of HSL by operating the Generation Resource at an Output Schedule for at least 30 minutes. In order to raise an output schedule above the seasonal HSL, the QSE may set the Resource telemetered HSL equal to its output temporarily for the purposes of the demonstration tests. After either a retest or a demonstration test, the MW capability of the Generation Resource based on the average of the MW production telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season. Any requested retest must take place within three Business Days after the request for retest.
(6) A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide hydro RRS shall evaluate the maximum capability of the Resource each Season.
(10) Before the start of each Season, a QSE shall provide ERCOT a list identifying each Controllable Load Resource that is expected to operate in a Season as a provider of Ancillary Service. Prior to the beginning of each Season, QSEs shall identify the Controllable Load Resources to be tested during the Season and the specific week of the test if known. Any Controllable Load Resource for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing Ancillary Services.
8.1.1.2.1.4 Voltage Support Service (VSS) Qualification
(3) Maximum lagging power factor reactive operating limit must be demonstrated during peak Load Season, at or above 95% of the most currently tested Net Dependable Capability, insofar as system voltage conditions and other factors will allow. The Generation Resource providing VSS is required to maintain this level of Reactive Power for 15 minutes.
11.4.3.2 Weather Sensitive Proxy Day Method
(a) To determine eligible proxy days, select all days (of matching weekday/weekend day type and season) within five degrees of the maximum temperature of the target Operating Day based on the previous 365 days and then limit the selection to those days that have their maximum temperatures occurring within two hours of the maximum temperature hour of occurrence of the Operating Day. The maximum temperature separation criterion provides initial assurance that the eligible day will have a similar diurnal temperature pattern as the target Settlement Operating Day.
16.11.4.1 Determination of Total Potential Exposure for a Counter-Party
SAF = Seasonal Adjustment Factor – Used to provide for the potential for seasonal price increases based on historical trends. ERCOT shall initially set this factor equal to 100%. This factor will not go below 100%. ERCOT will provide Notice to Market Participants of any change at least 14 days prior to effective date along with the analysis supporting the change.
18.7.1.2 Methodology for Load Profiling of Time Of Use
(b) Upon agreement between the Competitive Retailer (CR) and Transmission Service Provider (TSP) and/or Distribution Service Provider (DSP), a Time of Use Schedule (TOUS) is submitted by the TSP and/or DSP to the ERCOT Data Aggregation System (DAS), which identifies the TOU period associated with each Settlement Interval. The number of TOU periods is determined by the number of periods for which the meter will capture kWh. These periods may include on-peak, off-peak, and shoulder periods. The DAS shall collect and maintain the attributes of the TOUS (e.g. start and stop time, day of the week, and season.).
Section 22 Notification of Suspension of Operations of a Generation Resource
Seasonal Net Max Sustainable Rating – Summer (MW):
Seasonal Net Minimum Sustainable Rating – Summer (MW):