## 1) General Information
Sharyland Utilities L.P.
Distribution Loss Factor for 2007
General Information on Distribution Loss Factor:
The Distribution Loss Factor provides a mechanism to apply the forecast distribution losses of a Distribution Service Provider to the
individual loads served in the DSP's Service Territory.
This process is explained in ERCOT Protocols Section 13: Transmission and Distribution Losses, which was revised in September, 2006.
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2007 = 8,794 MWH
Customer Coding for Sharyland Utilities:
Distribution customers that take service at secondary voltage are coded "A"
Sharyland Utilities has no customers served from the transmission system.
For "A" Secondary Customers
F1 = | 0.0072
F2 = | 0.0005
F3 = | 0.0139
AAL for ERCOT (15 mins) = 8,794
Assumptions
ERCOT peak load and AAL for ERCOT are proportionately similar to Sharyland Utilities.
|  |  |  | For 15 Min |  | For 1 Hour
|  |  |  | AAL | Peak | AAL | Peak
|  |  | ERCOT | 8793.8397 | 15607.37 | 35175.3587 | 62429.48
|  |  | Sharyland Utilities | 2.1791 | 3.8675 | 8.7164 | 15.47
ERCOT Peak was at 8/17/2006 at 17:00
SU Coincident Peak at 8/17/2006 at 17:00 was 15.47 MW.
SU System Peak actually occurred 8/30/2006 at 1630 hours was 16.0 MW
For this analysis it is reasonable to assume ERCOT peak and the SU Peak are proportionate
Methodology upon which the calculation of loss factor was made:
Loss equations utilized to determine the loss for each component of the Sharyland system including distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses.
The following formula was solved for each component with B representing no load losses while A is a constant used to determine load losses
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated as follows.
1. Substation Transformer Losses
Sharyland presently has two distribution station transformers; Taylor and Bentsen
The total no-load losses for these units in 2006 is 55.52 kW or 0.0555 MW
The full load losses for each transformer was used to determine the load losses.
The basis for the load losses was the actual 15 minute demands on each transformer.
The peak substation transformer load losses that occur at the system peak of 15.47 MW is 0.0208 MW.
This resulted in a total of 0.0763 MW of substation transformer losses at approximately 15.47 MW.
The constants in the system loss equations were adjusted to match this result. See Tab 3) Loss Analysis 2007.
2. Primary Conductor Losses
A computer model (Milsoft) of the distribution system was loaded with the actual feeder demands and power factor at the time of the
ERCOT and SU peak. The loading was evenly distributed throughout the model. The resulting analysis
provided the kW losses at that peak demand value of 15.47 MW which was 86 kW.
The constants (A&B) were determined using the Tab 4) Loss Equations
The factor A was verified at half of the peak demand and was found to be within 1% of the actual value.
3. Distribution Transformer Losses
An inventory of the distribution transformers was determined. Average values by size transformer
were determined for the "No-load" losses and "Full Load" losses. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
The "Load" losses were calculated using a utilization factor which is the ratio of peak demand to total transformer capacity.
As the system load grows it is anticipated that the utilization factor will increase in future years.
4. Secondary Conductor Losses
Secondary and service losses were calculated based on the average service lengths and average number of consumers on secondary
conductors. These averages were obtained on a random take-off from the system maps. The load per consumer was estimated
by dividing total load by the number of consumers.
Overall results:
2007
For "A" Secondary Customers |  |  | DLF at AAL | 2.15%
|  |  | DLF at ERCOT Peak | 2.113%
DLF Coefficients (F1, F2 and F3)
The F1, F2 and F3 coefficients developed for secondary customer. These coefficients were selected to provide a curve fit with the loss equations
that were developed above. The graph in Tab 5) Graphs and in Tab 3 Loss Analysis 2007 depict the curve fitting.
| F1 = | 0.0072
| F2 = | 0.0005
| F3 = | 0.0139

## 2) ERCOT Load Comparison
ERCOT / Sharyland Utilities Loading Comparison For 2006
Peak Load | 2006
ERCOT peak (MW) = | 62429.5 | (on 8/17/2006 at 17:00)
Peak Interval = | 15607.37
SU peak (MW) = | 15.47 | (on 8/17/2006 at 16:31)
Peak interval = | 3.8675 | 0.02478% | = SU peak relative to ERCOT peak
Average Annual Load (AAL)
ERCOT Annual Total System MWH = | 308136141.9135 | (for 9/1/2005 - 8/31/2006)
Intervals per year = | 35040
AAL value = | 8793.8397 | for 15 mins | 35175.3587 | for 1 hour
Assume AAL (Average Annual Load) for SU is proportional to peak in a manner that is similar to ERCOT.
The calculation below confirms this simplifying assumption.
AAL for SU would correspond to | 2.1791 | for 15 mins | 8.7164 | for 1 hour
SU Annual Total System Purchases | 74369.079 | (9/1/2005-8/31/2006)
Intervals per year = | 35040
AAL value = | 2.1224 | for 15 mins | 8.4896 | for 1 hour

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 3) Loss Analysis 2007
|  | Sharyland Utilities Distribution Loss Factor For 2007 | [13 empty] | Using F1, F2 & F3 Coefficients
ERCOT | ERCOT |  | SU | SU |  |  | Primary | Total | Total |  |  |  | Secondary
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | DLF
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | Secondary
SIEL
|  |  |  | 0.25 | 0.055527 | 0.19447 | 1.3432e-05 | 0.055541 | 22.22% | 0.19446 | 0.06721 | 0.12725 | 3.2782e-06 | 0.12275 | 49.1%
|  |  |  | 0.5 | 0.055544 | 0.44446 | 7.0161e-05 | 0.055614 | 11.12% | 0.44439 | 0.067246 | 0.37714 | 2.8796e-05 | 0.12289 | 24.58%
|  |  |  | 0.75 | 0.055571 | 0.69443 | 0.00017128 | 0.055742 | 7.432% | 0.69426 | 0.06731 | 0.62695 | 7.9578e-05 | 0.12313 | 16.42%
1008.8982 | 4035.5926 |  | 0.25 | 1 | 0.055609 | 0.94439 | 0.00031677 | 0.055926 | 5.593% | 0.94407 | 0.067401 | 0.87667 | 0.0001556 | 0.12348 | 12.35% | 12.25%
1513.3472 | 6053.389 | 1 | 0.375 | 1.5 | 0.055718 | 1.4443 | 0.00074087 | 0.056459 | 3.764% | 1.4435 | 0.067668 | 1.3759 | 0.00038326 | 0.12451 | 8.301% | 8.251%
2017.7963 | 8071.1853 | 2 | 0.5 | 2 | 0.05587 | 1.9441 | 0.0013424 | 0.057212 | 2.861% | 1.9428 | 0.068046 | 1.8747 | 0.00071156 | 0.12597 | 6.299% | 6.273%
2522.2454 | 10088.9816 | 3 | 0.625 | 2.5 | 0.056066 | 2.4439 | 0.0021214 | 0.058187 | 2.327% | 2.4418 | 0.068536 | 2.3733 | 0.0011403 | 0.12786 | 5.115% | 5.103%
3026.6945 | 12106.7779 | 4 | 0.75 | 3 | 0.056305 | 2.9437 | 0.0030777 | 0.059383 | 1.979% | 2.9406 | 0.069136 | 2.8715 | 0.0016693 | 0.13019 | 4.34% | 4.336%
3531.1436 | 14124.5743 | 5 | 0.875 | 3.5 | 0.056588 | 3.4434 | 0.0042113 | 0.060799 | 1.737% | 3.4392 | 0.069847 | 3.3694 | 0.0022984 | 0.13294 | 3.798% | 3.801%
4035.5926 | 16142.3706 | 6 | 1 | 4 | 0.056914 | 3.9431 | 0.0055222 | 0.062436 | 1.561% | 3.9376 | 0.07067 | 3.8669 | 0.0030273 | 0.13613 | 3.403% | 3.409%
4540.0417 | 18160.1669 | 7 | 1.125 | 4.5 | 0.057283 | 4.4427 | 0.0070103 | 0.064294 | 1.429% | 4.4357 | 0.071603 | 4.3641 | 0.0038559 | 0.13975 | 3.106% | 3.114%
5044.4908 | 20177.9632 | 8 | 1.25 | 5 | 0.057697 | 4.9423 | 0.0086756 | 0.066372 | 1.327% | 4.9336 | 0.072646 | 4.861 | 0.0047839 | 0.1438 | 2.876% | 2.886%
5548.9399 | 22195.7596 | 9 | 1.375 | 5.5 | 0.058153 | 5.4418 | 0.010518 | 0.068671 | 1.249% | 5.4313 | 0.0738 | 5.3575 | 0.0058111 | 0.14828 | 2.696% | 2.707%
6053.389 | 24213.5559 | 10 | 1.5 | 6 | 0.058653 | 5.9413 | 0.012537 | 0.071191 | 1.187% | 5.9288 | 0.075064 | 5.8537 | 0.0069374 | 0.15319 | 2.553% | 2.565%
6557.8381 | 26231.3522 | 11 | 1.625 | 6.5 | 0.059197 | 6.4408 | 0.014734 | 0.073931 | 1.137% | 6.4261 | 0.076438 | 6.3496 | 0.0081626 | 0.15853 | 2.439% | 2.451%
7062.2871 | 28249.1485 | 12 | 1.75 | 7 | 0.059784 | 6.9402 | 0.017107 | 0.076891 | 1.098% | 6.9231 | 0.077922 | 6.8452 | 0.0094864 | 0.1643 | 2.347% | 2.359%
7566.7362 | 30266.9449 | 13 | 1.875 | 7.5 | 0.060415 | 7.4396 | 0.019658 | 0.080072 | 1.068% | 7.4199 | 0.079516 | 7.3404 | 0.010909 | 0.1705 | 2.273% | 2.285%
8071.1853 | 32284.7412 | 14 | 2 | 8 | 0.061089 | 7.9389 | 0.022385 | 0.083474 | 1.043% | 7.9165 | 0.081219 | 7.8353 | 0.012429 | 0.17712 | 2.214% | 2.225%
8575.6344 | 34302.5375 | 15 | 2.125 | 8.5 | 0.061806 | 8.4382 | 0.025289 | 0.087096 | 1.025% | 8.4129 | 0.083032 | 8.3299 | 0.014048 | 0.18418 | 2.167% | 2.178%
9080.0835 | 36320.3338 | 16 | 2.25 | 9 | 0.062567 | 8.9374 | 0.02837 | 0.090938 | 1.01% | 8.9091 | 0.084954 | 8.8241 | 0.015764 | 0.19166 | 2.13% | 2.14%
9584.5325 | 38338.1301 | 17 | 2.375 | 9.5 | 0.063372 | 9.4366 | 0.031628 | 0.095 | 1% | 9.405 | 0.086986 | 9.318 | 0.017578 | 0.19956 | 2.101% | 2.11%
10088.9816 | 40355.9265 | 18 | 2.5 | 10 | 0.06422 | 9.9358 | 0.035062 | 0.099283 | 0.9928% | 9.9007 | 0.089126 | 9.8116 | 0.01949 | 0.2079 | 2.079% | 2.088%
10593.4307 | 42373.7228 | 19 | 2.625 | 10.5 | 0.065112 | 10.4349 | 0.038674 | 0.10379 | 0.9884% | 10.3962 | 0.091376 | 10.3048 | 0.021499 | 0.21666 | 2.063% | 2.071%
11097.8798 | 44391.5191 | 20 | 2.75 | 11 | 0.066047 | 10.934 | 0.042461 | 0.10851 | 0.9864% | 10.8915 | 0.093734 | 10.7978 | 0.023605 | 0.22585 | 2.053% | 2.06%
11602.3289 | 46409.3154 | 21 | 2.875 | 11.5 | 0.067025 | 11.433 | 0.046426 | 0.11345 | 0.9865% | 11.3865 | 0.0962 | 11.2903 | 0.025807 | 0.23546 | 2.047% | 2.053%
12106.7779 | 48427.1118 | 22 | 3 | 12 | 0.068047 | 11.932 | 0.050566 | 0.11861 | 0.9884% | 11.8814 | 0.098776 | 11.7826 | 0.028107 | 0.2455 | 2.046% | 2.051%
12611.227 | 50444.9081 | 23 | 3.125 | 12.5 | 0.069113 | 12.4309 | 0.054884 | 0.124 | 0.992% | 12.376 | 0.10146 | 12.2745 | 0.030503 | 0.25596 | 2.048% | 2.052%
13115.6761 | 52462.7044 | 24 | 3.25 | 13 | 0.070222 | 12.9298 | 0.059377 | 0.1296 | 0.9969% | 12.8704 | 0.10425 | 12.7662 | 0.032995 | 0.26684 | 2.053% | 2.056%
13620.1252 | 54480.5007 | 25 | 3.375 | 13.5 | 0.071374 | 13.4286 | 0.064047 | 0.13542 | 1.003% | 13.3646 | 0.10715 | 13.2574 | 0.035584 | 0.27816 | 2.06% | 2.063%
14124.5743 | 56498.2971 | 26 | 3.5 | 14 | 0.07257 | 13.9274 | 0.068894 | 0.14146 | 1.01% | 13.8585 | 0.11016 | 13.7484 | 0.038268 | 0.28989 | 2.071% | 2.072%
14629.0233 | 58516.0934 | 27 | 3.625 | 14.5 | 0.07381 | 14.4262 | 0.073917 | 0.14773 | 1.019% | 14.3523 | 0.11327 | 14.239 | 0.041048 | 0.30205 | 2.083% | 2.083%
15133.4724 | 60533.8897 | 28 | 3.75 | 15 | 0.075093 | 14.9249 | 0.079116 | 0.15421 | 1.028% | 14.8458 | 0.1165 | 14.7293 | 0.043923 | 0.31463 | 2.098% | 2.097%
15637.9215 | 62551.686 | 29 | 3.875 | 15.5 | 0.076419 | 15.4236 | 0.084491 | 0.16091 | 1.038% | 15.3391 | 0.11983 | 15.2193 | 0.046894 | 0.32763 | 2.114% | 2.112%
16142.3706 | 64569.4823 | 30 | 4 | 16 | 0.077789 | 15.9222 | 0.090042 | 0.16783 | 1.049% | 15.8322 | 0.12326 | 15.7089 | 0.04996 | 0.34106 | 2.132% | 2.129%
16646.8197 | 66587.2787 | 31 | 4.125 | 16.5 | 0.079202 | 16.4208 | 0.095769 | 0.17497 | 1.06% | 16.325 | 0.12681 | 16.1982 | 0.053121 | 0.3549 | 2.151% | 2.147%
17151.2687 | 68605.075 | 32 | 4.25 | 17 | 0.080659 | 16.9193 | 0.10167 | 0.18233 | 1.073% | 16.8177 | 0.13046 | 16.6872 | 0.056377 | 0.36917 | 2.172% | 2.167%
17655.7178 | 70622.8713 | 33 | 4.375 | 17.5 | 0.08216 | 17.4178 | 0.10775 | 0.18991 | 1.085% | 17.3101 | 0.13422 | 17.1759 | 0.059727 | 0.38386 | 2.193% | 2.188%
18160.1669 | 72640.6676 | 34 | 4.5 | 18 | 0.083704 | 17.9163 | 0.11401 | 0.19771 | 1.098% | 17.8023 | 0.13808 | 17.6642 | 0.063171 | 0.39897 | 2.216% | 2.21%
8794 | 35176 | AAL | 2.1791 | 8.7164 | 0.06213 | 8.6543 | 0.026601 | 0.088732 | 1.018% | 8.6277 | 0.083851 | 8.5439 | 0.014779 | 0.18736 | 2.15%
15607.375 | 62429.5 | Peak | 3.8675 | 15.47 | 0.076338 | 15.3937 | 0.084163 | 0.1605 | 1.038% | 15.3095 | 0.11962 | 15.1899 | 0.046713 | 0.32684 | 2.113%
For Secondary Distribution Customers "A"
Secondary Constants
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant |  |  | F1 = | 0.0072 | right
|  |  | 2007 Values ----> | 0.055522 | 8.6981e-05 | 0 | 0.00035517 |  |  | 0.067202 | 0.00022366 | 0 | 0.00020246 | <--- 2007 Values |  | F2 = | 0.0005 | middle
[16 empty] | F3 = | 0.0139 | left
DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
AAL for ERCOT (15 mins) = 8,794
Secondary Constants
F1 = | 0.0072 | right
F2 = | 0.0005 | middle
F3 = | 0.0139 | left
Note on B10: Kevin Mara: Ratio the Ercot Loading to the Assumed Loading in Col E by using the ratio of the AALs
Note on E10: Kevin Mara: Assumed loading
Note on E47: Kevin Mara: AAL for 1 hour interval same ratio as 15 min AAL to Peak
Note on E48: Kevin Mara: Peak Demand, coincident with ERCOT Peak Demand-8-17-06, 1700 hours
Note on G10: Kevin Mara: Assumed Load (col E) less Sub Transf losses yields input into distrib system

## 4) Loss Equations
System Loss Equations For Sharyland Utilities
Sharyland Utilities Loss Values
| Losses = | AX2 + B
|  | A = Constant | [6 empty] | Coincident Peak Loading (MW) | Coincident Peak Loading (kW)
|  | B = Constant | [6 empty] | 15.47 | 15470
X = Input to System (MW)
Substation Transformers |  |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW) | Total Losses (kW)
| A = | 8.6981e-05 |  |  | 0.076338 | 8.6981e-05 | 0.055522 | 15.47 | 0.055522 | 0.020816 | 55.5276 | 20.8163 | 76.3439
| B = | 0.055522 | Total No-Load Losses For Substation Transformers = .055522 MW
Primary Conductor |  |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 0.00035517 |  | Case 1 at Peak | 0.085 | 0.00035517 | 0 | 15.47 | 0 | 0.085 | 0 | 85 | 85
| B = | 0 |  | Case 2 at half Peak | 0.021 | 0.00035099 | 0 | 7.735 | 0 | 0.021 | 0 | 21
[5 empty] | Error = | 1.19%
Distribution Transformers |  |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 0.00022366 |  |  | 0.12073 | 0.00022366 | 0.067202 | 15.47 | 0.067202 | 0.053527 | 67.202 | 53.5267 | 120.7287
| B = | 0.067202 | Total No-Load Losses For Distribution Transformers = 0.0672 MW
Secondary Conductor |  |  |  |  | Losses | A | B | X | No Load Losses (MW) | Load Losses (MW) | No Load Losses (kW) | Load Losses (kW)
| A = | 0.00020246 |  |  | 0.048452 | 0.00020246 | 0 | 15.47 | 0 | 0.048452 | 0 | 48.452 | 48.452
| B = | 0
330.5245
2.137%

## 6) Power Xfmr Losses
|  |  | TAYLOR SUBSTATION | [9 empty] | BENTSEN SUBSTATION | [9 empty] | TOTAL SYSTEM
Cell # | DATE | TIME | Taylor MW Demand | Taylor MVAR Demand | Taylor Power Factor | XMFR No Load Loss (MW) | XMFR No Load Loss (MWH) | XMFR Full Load Losses @ 30 MVA (MW) | XFMR Load Losses (MW) | XFMR Load Losses (MWH) | Total Taylor Transformer Losses (MW) | Total Taylor Transformer Losses (MWH) | Bentsen Demand (MW) | Bentsen Reactance (MVar) | Bentsen Power Factor | XMFR No Load Loss (MW) | XMFR No Load Loss (MWH) | XMFR Full Load Losses @ 30 MVA (MW) | XFMR Load Losses (MW) | XFMR Load Losses (MWH) | Total Bentsen Transformer Losses (MW) | Total Bentsen Transformer Losses (MWH) | Total Transformer No Load Losses (MW) Taylor + Bensten | Total Transformer Load Losses(MW) Taylor + Bensten | Total Transformer Losses(MW) Taylor + Bensten | Total Transformer Losses(MWH) Taylor + Bensten | System Demand (MW) | Factor A for Each Hour | Factor A at Peak | Margin of Error on Factor A: Average Error is -3.4%
21959 | 2006-08-17 | 17:00 | 8.61 | 3.02 | 0.94364 | 0.02813 | 0.0070325 | 0.12943 | 0.011973 | 0.0029932 | 0.040103 | 0.010026 | 6.86 | 3.8 | 0.87476 | 0.027392 | 0.006848 | 0.12942 | 0.0088436 | 0.0022109 | 0.036236 | 0.0090589 | 0.055522 | 0.020816 | 0.076338 | 0.019085 | 15.47 | 8.6981e-05 | 8.6981e-05 | 0%
Reference file Sharyland Power XFMR Losses 11_2_2006.xls
That file contains the 15 minute demand data for 10 months of history.
For space this data has been saved separately

## 7) Distribution Line Losses
Sharyland peak (MW) (on 8/17/2006 at 17:00)
Feeder Number | DATE | TIME | 3 Phase Demand in kW | 3 Phase KVAR | PF | Modeled Dist. Losses (kW) * | Modeled Dist. Losses (% of Actual Peak Demand)
T1-111 | 2006-08-17 | 17:00 | 1376 | 394 | 96.14% | 2 | 0.1453%
T1-114 | 2006-08-17 | 17:00 | 4840 | 1547 | 95.25% | 28 | 0.5785%
T1-115 | 2006-08-17 | 17:00 | 2367 | 902 | 93.45% | 12 | 0.507%
T1-211 | 2006-08-17 | 17:00 | 3858 | 1228 | 95.29% | 30 | 0.7776%
T1-215 | 2006-08-17 | 17:00 | 2948 | 2441 | 77.02% | 13 | 0.441%
|  |  | 15389 | 6512 | 92.09% | 85 | 0.5523%
|  | Highside Demand at Substations= | 15470
|  |  | 81 | kW losses through the transformers. (15,470 less 15,389)
Correlates with the calculated value of 76 kW in substation transformer losses
* Data from Milsoft model of the distribution system. Assumes uniform loading of the line sections.

## 8) Distribution Xfmr Losses
Peak Distribution XFMR Losses
XFMR Type | XFMR KVA | Quantity | Total Installed kVA | Average No Load Loss per Transf (kW) | Average Full Load Loss per Transf (kW) | Utilization Factor * | Total No Load Losses (kW) | Total Peak Losses (kW) ** | Total Transformer Losses (kW)
Overhead XFMRS | 10 | 11 | 110 | 0.037 | 0.141 | 0.36187 | 0.407 | 0.2031 | 0.6101
Overhead XFMRS | 15 | 9 | 135 | 0.045 | 0.195 | 0.36187 | 0.405 | 0.22982 | 0.63482
Overhead XFMRS | 25 | 1 | 25 | 0.078 | 0.253 | 0.36187 | 0.078 | 0.03313 | 0.11113
|  | Total: | 270
Padmounted XFMRS 1ph | 25 | 27 | 675 | 0.048 | 0.36 | 0.36187 | 1.296 | 1.2728 | 2.5688
Padmounted XFMRS 1ph | 50 | 219 | 10950 | 0.088 | 0.548 | 0.36187 | 19.272 | 15.7156 | 34.9876
Padmounted XFMRS 1ph | 75 | 86 | 6450 | 0.127 | 0.647 | 0.36187 | 10.922 | 7.2863 | 18.2083
Padmounted XFMRS 1ph | 100 | 12 | 1200 | 0.165 | 0.745 | 0.36187 | 1.98 | 1.1707 | 3.1507
|  | Total: | 19275
Padmounted XFMRS 3ph | 75 | 3 | 225 | 0.157 | 0.618 | 0.36187 | 0.471 | 0.24278 | 0.71378
Padmounted XFMRS 3ph | 150 | 6 | 900 | 0.266 | 1.485 | 0.36187 | 1.596 | 1.1668 | 2.7628
Padmounted XFMRS 3ph | 300 | 11 | 3300 | 0.37 | 2.315 | 0.36187 | 4.07 | 3.3347 | 7.4047
Padmounted XFMRS 3ph | 500 | 8 | 4000 | 0.595 | 4.157 | 0.36187 | 4.76 | 4.3549 | 9.1149
Padmounted XFMRS 3ph | 750 | 5 | 3750 | 0.866 | 4.821 | 0.36187 | 4.33 | 3.1566 | 7.4866
Padmounted XFMRS 3ph | 1000 | 5 | 5000 | 1.247 | 7.509 | 0.36187 | 6.235 | 4.9165 | 11.1515
Padmounted XFMRS 3ph | 1500 | 5 | 7500 | 1.695 | 11.94 | 0.36187 | 8.475 | 7.8177 | 16.2927
Padmounted XFMRS 3ph | 2500 | 1 | 2500 | 2.905 | 20.047 | 0.36187 | 2.905 | 2.6252 | 5.5302
|  | Total: | 27175 |  |  |  | 67.202 | 53.5267 | 120.7287
|  | Total kVA Capacity | 46720
|  | Total kW Demand | 15470 |  | ** Peak Losses = (# of units )(Full load losses)(Utilization factor)^2
|  | Total kVar Demand | 6820
|  | Total kVA Demand | 16906.6052
| * | Utilization Factor | 0.36187

## 9) Secondary Losses
|  | Length in Feet | Number of Cable Sections | Number of Customers per Cable Section (5) | Load in kVA per Cable Section (1) and (5) | Load Current at 240 volts | Power Factor of Load Current (1) | Cable Resistance per 1,000 feet (2) | Cable Reactance per 1,000 feet (2) | Voltage Drop per Cable Section in volts (3) | Line Losses in watts per Cable Section | Total Losses in all Cable Sections (kW)
| 4/0AL Service Run (one home) | 35 | 1733 | 1 | 9.58 | 39.9 | 0.915 | 0.099943 | 0.024681 | 0.28323 | 11.3007 | 19.5842
| 350AL Secondary Run (1.66 homes) | 83 | 606 | 1.66 | 15.9028 | 66.3 | 0.915 | 0.060549 | 0.024492 | 0.7185 | 47.6367 | 28.8678
[11 empty] | Total Secondary and Service Losses | 48.452
(1) | Sharyland System Demand |  | Demand less pwr xfmr, dist line, and dist xfmr losses
| Total kW Demand | 15470 | 15191.3156
| Total kVar Demand | 6820
| Total kVA Demand | 16906.6052 | 16602.0411
| System Power Factor | 0.91503
| Number of Consumers |  | 1733
| Coincident Peak Load/Consumer (kVA) |  | 9.58
| Assumed Power Factor |  | 0.915
Impedance Values of 600 volt Triplexed Cable
(2) | Triplex Conductor Size | Conductor Diameter (in.) | Insulation Thickness (in.) | Cable Diameter (in.) | A-C Resistance (ohms/1000 ft) | Inductive Reactance (ohms/1000 ft)
| 4/0 AL | 0.578 | 0.08 | 0.658 | 0.099943 | 0.024681
| 350 MCM | 0.736 | 0.095 | 0.831 | 0.060549 | 0.024492
Inductive Reactance Formula (ohms per 1,000 ft.)
Xh=(2*pi*f/1000)*{.0153+.1404*log base 10 (s/r)}
Where:
|  | Xh | Inductive reactance to neutral of one conductor in ohms per 1,000 ft.
|  | f | frequency in hertz (60 hertz)
|  | s | Spacing between the centers of the conductor in inches
|  | r | Radius of the metal portion of the conductor in inches
(3) | Secondary/Service Voltage Drop
Vdservice = (Ih)*(PF)[(Rh)*(2)*(L/1000)]+(Ih)[sin(cos-1(PF))]*{(Xh)*(2)*(L/1000)}
Where:
| Vdservice = | Voltage drop through service conductor in volts
| Ih = | Load current
| kV= | 0.240 kV
| PF= | Power factor of load current expressed as a decimal
| Rh= | Resistance of the service in ohms per 1,000 feet
| Xh= | Reactance of the service in ohms per 1,000 feet
| L= | Length of service conductor
(4) | Secondary/Service Voltage Drop
Power Losses = V*Ih
Where:
| V = | Voltage drop through service conductor in volts
| Ih = | Load current
(5) | Estimate of Secondary and Services
Subdivision Takeoff
La Quinta
| Lots | 175
Typically :
1 XFMR=2 services, with Secondary to 2 pedestals which serve 1-2 services each (total of 4-6 services per transformer)
Total of 6 services per XFMR
|  | Quantity | Consumers Per
| XFMR Count | 39 | 2
| Pedestals | 65 | 1.6615
| Served From | XFMR | Pedestal | Total
| Services | 78 | 108 | 186
|  | 41.94% | 58.06%

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified