## Calculation Data
Table 1: NEC Data
Definition | Name | Value | Units | Equation
NEC total 2005 purchases | ATM | 255671.563 | MWH | metered
NEC total 2005 sales | ATMS | 232098.657 | MWH | metered
Primary account estimated annual sales 2005 | PATMS | 8893.38 | MWH | metered
Secondary account estimated annual sales 2005 | SATMS | 223205.277 | MWH | ATMS-PATMS
Primary account system no load loss | PNLL | 9.5436 | kWatt | (PATMS/ATMS)*(TNLL)
Secondary account dist xfmr NEC 2005 no load loss | SNLL | 988.35 | kWatt | compiled
Secondary account system no load loss | SCNLL | 1227.8744 | kWatt | SNLL+(SATMS/ATMS)*TNLL
STEC transformer and regulator no load loss | TNLL | 249.068 | kWatt | compiled
NEC Distribution transformer load losses at Average Annual Load | DTLL | 28.22 | kWatt
Primary account scale factor | PSF | 0.63231 | na | ((ATM-ATMS)-((SNLL+((PATMS/ATMS)*DTLL))*8760/1000))/(ATM-ATMS)
| F1 | F2 | F3
Secondary Metered Account Factors | 0.005 | 0.001 | 0.059 | Code B
Primary Metered Account Factors | 0.0031616 | 0.00063231 | 0.037307 | Code A