| NPRR Number | 423 | NPRR Title | Add Voltage Support Requirement for IRRs and Allow SCADA Control of Static VAr Devices if Approved by ERCOT (formerly “Add Voltage Support Requirement for IRRs and Allow Manual Control of Static VAr Devices if Approved by ERCOT”) |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved |
| Date of Decision |  | February 21, 2012 |  |  |
| Effective Date |  | March 1, 2012 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Section Requiring Revision |  | 3.15, Voltage Support |  |  |
| Market Guide Section(s) Requiring Revision |  | None. |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) includes Intermittent Renewable Resources (IRRs) in the voltage requirement and clarifies the reactive requirement to be the same as Wind-powered Generation Resources (WGRs). This NPRR also proposes that switchable static Volt-Ampere reactive (VAr) devices can be Supervisory Control and Data Acquisition (SCADA) controlled if approved by ERCOT. |  |  |
| Reason for Revision |  | Similar to WGRs, solar power plants cannot have or have very limited reactive capability at output less than 10%. This NPRR will clarify the Reactive Power requirement for solar power plants. Paragraph (8) of Section 3.15 allows Generation Entities to submit ERCOT-specific proposals to meet the Reactive Power requirements. Depending on the location and size of those proposed static VAr devices, the Transmission Service Provider (TSP) may suggest that those devices are in the SCADA control mode to avoid undesired ERCOT System impacts, such as voltage swing during the switching of those VAr devices. This NPRR provides a solution for those proposed VAr devices operating in the SCADA control mode based on the agreement between the Generation Resource and TSP |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR423 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 11/2/11, NPRR423 and the associated Impact Analysis were posted. - On 11/14/11, Oncor Electric Delivery comments were posted. - On 11/17/11, PRS considered NPRR423. - On 12/15/11, PRS considered the 11/17/11 PRS Report and Impact Analysis for NPRR423. - On 1/5/12, TAC considered NPRR423. - On 2/21/12, the ERCOT Board considered NPRR423. |  |  |
| PRS Decision |  | On 11/17/11, PRS unanimously voted to recommend approval of NPRR423 as amended by the 11/14/11 Oncor Electric Delivery comments and as revised by PRS. All Market Segments were present for the vote. On 12/15/11, PRS unanimously voted to endorse and forward the 11/17/11 PRS Report and Impact Analysis for NPRR423 to TAC. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 11/17/11, PRS discussed revisions to align language with the current practice of allowing static VAr devices to be switched via SCADA if agreed upon by the Generation Resource and the TSP. On 12/15/11, there was no discussion. |  |  |
| TAC Decision |  | On 1/5/12, TAC unanimously voted to recommend approval of NPRR423 as recommended by PRS in the 12/15/11 PRS Report. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 1/5/12, there was no discussion. |  |  |
| ERCOT Opinion |  | ERCOT supports the approval of NPRR423. |  |  |
| Board Decision |  | On 2/21/12, the ERCOT Board approved NPRR423 as recommended by TAC in the 1/5/12 TAC Report. |  |  |

| Business Case |  |  |
| --- | --- | --- |
| Business Case | 1 | Benefits: - To clarify the solar power Resource voltage support requirement. - Provide a solution to allow SCADA control of static VAr devices and avoid undesired ERCOT System impact on voltage with automatic control of static VAr devices. |
|  | 2 | Impacts to Generation Resources: - Generation Resources will have a clear understanding of the voltage support requirement of IRRs (wind and solar) |
|  | 3 | Impacts to TSPs: - TSP can recommend the control mode of the static VAr devices to avoid undesired ERCOT System impact, such as voltage swing due to the frequent switching of the automatic controlled static VAr devices. |

| Sponsor |  |
| --- | --- |
| Name | Isabel Flores/Shun-Hsien (Fred) Huang |
| E-mail Address | IFlores@ercot.com/shuang@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6531/512-248-6665 |
| Cell Number |  |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sonja B. Mingo |
| E-Mail Address | smingo@ercot.com |
| Phone Number | 512-248-6463 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Oncor Electric Delivery 111411 | Proposed modifications to specify that static VAr devices can be manually switchable using supervisory control. |

Comments

Please note that NPRR366, Generation Resource Power Factor Criteria Clarification, also proposes revisions to Section 3.15.

Proposed Protocol Language Revision

3.15	Voltage Support

(1)	ERCOT in coordination with the Transmission Service Providers (TSPs) shall establish and update, as necessary, the ERCOT System Voltage Profile for all Electrical Buses used for Voltage Support in the ERCOT System and shall post all Voltage Profiles on the Market Information System (MIS) Secure Area.  ERCOT may temporarily modify its requirements based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT. Generation Resources shall comply with the following Reactive Power Requirements:  an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.  The Reactive Power requirements shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability.  As part of the technical Resource requirements to begin commercial operations, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this paragraph.  Any study or testing results must be accepted by ERCOT prior to commercial operations.  The Reactive Power requirements of this paragraph shall apply to all Generation Resources except as otherwise provided in paragraphs (4) through (6) below.

(4)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: (i) the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or (ii) Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion;

(ii)	Existing Non-Exempt WGRs shall update any and all Resource registration information regarding their Reactive Power capability documented by the engineering study results or testing results;

(iii) 	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource registration information regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource registration information supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) and (4) above, multiple generation units including wind turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).   ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	WGRs must provide a Real-Time Supervisory Control and Data Acquisition (SCADA) point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

WGRs must comply with the requirements of paragraph (12) by no later than June 1, 2010.

(13)	For the purpose of complying with the Reactive Power requirements under this Section, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.